Copyright 2013 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 072100 - THERMAL INSULATION

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

SUMMARY

Section Includes:

Extruded polystyrene foam-plastic board.

Molded polystyrene foam-plastic board.

Polyisocyanurate foam-plastic board.

Glass-fiber blanket.

Glass-fiber board.

Mineral-wool blanket.

Mineral-wool board.

ACTION SUBMITTALS

Product Data: For each type of product.

LEED Submittals:

Product Data for Credit MR 4: For products having recycled content, documentation indicating percentages by weight of postconsumer and preconsumer recycled content. Include statement indicating cost for each product having recycled content.

"Laboratory Test Reports for Credit IEQ 4.6" Subparagraph below applies to LEED for Schools.

Laboratory Test Reports for Credit IEQ 4.6: For glass-fiber insulation products, documentation indicating that products comply with the testing and product requirements of the California Department of Public Health's (formerly, the California Department of Health Services') "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Retain paragraph below for glass-fiber insulation required to be low emitting.

Low-emitting product certification.

INFORMATIONAL SUBMITTALS

Product test reports.

Research reports.

PRODUCTS

Manufacturers and products listed in SpecAgent and Masterworks Paragraph Builder are neither recommended nor endorsed by the AIA or ARCOM. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

EXTRUDED POLYSTYRENE FOAM-PLASTIC BOARD

Extruded polystyrene boards in this article are also called "XPS boards."

Insert drawing designations to identify each product. Use these designations on Drawings to show where each insulation type is required.

Extruded Polystyrene Board, Type X <Insert drawing designation>: ASTM C 578, Type X, 15-psi (104-kPa) minimum compressive strength; unfaced; maximum flame-spread and smoke-developed indexes of 25 and 450, respectively, per ASTM E 84.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Fire Propagation Characteristics" Subparagraph below if required. Tested products are not available from all manufacturers for all types of assemblies.

Fire Propagation Characteristics: Passes NFPA 285 testing as part of an approved assembly.

Extruded Polystyrene Board, Type IV <Insert drawing designation>: ASTM C 578, Type IV, 25-psi (173-kPa) minimum compressive strength; unfaced; maximum flame-spread and smoke-developed indexes of 25 and 450, respectively, per ASTM E 84.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Fire Propagation Characteristics" Subparagraph below if required. Tested products are not available from all manufacturers for all types of assemblies.

Fire Propagation Characteristics: Passes NFPA 285 testing as part of an approved assembly.

Extruded Polystyrene Board, Type VI <Insert drawing designation>: ASTM C 578, Type VI, 40-psi (276-kPa) minimum compressive strength; maximum flame-spread and smoke-developed indexes of 25 and 450, respectively, per ASTM E 84.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Extruded Polystyrene Board, Type VII <Insert drawing designation>: ASTM C 578, Type VII, 60-psi (414-kPa) minimum compressive strength; maximum flame-spread and smoke-developed indexes of 25 and 450, respectively, per ASTM E 84.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Extruded Polystyrene Board, Type V <Insert drawing designation>: ASTM C 578, Type V, 100-psi (690-kPa) minimum compressive strength; maximum flame-spread and smoke-developed indexes of 25 and 450, respectively, per ASTM E 84.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

MOLDED POLYSTYRENE FOAM-PLASTIC BOARD

Molded polystyrene boards in this article are also called "EPS boards," "expanded polystyrene boards," or "beadboards."

Insert drawing designations to identify each product. Use these designations on Drawings to show where each insulation type is required.

Molded Polystyrene Board, Type I <Insert drawing designation>: ASTM C 578, Type I, 10-psi (69-kPa) minimum compressive strength.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Molded Polystyrene Board, Type VIII <Insert drawing designation>: ASTM C 578, Type VIII, 13-psi (90-kPa) minimum compressive strength.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Molded Polystyrene Board, Type II <Insert drawing designation>: ASTM C 578, Type II, 15-psi (104-kPa) minimum compressive strength.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Molded Polystyrene Board, Type IX <Insert drawing designation>: ASTM C 578, Type IX, 25-psi (173-kPa) minimum compressive strength.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

POLYISOCYANURATE FOAM-PLASTIC BOARD

Insert drawing designations to identify each product. Use these designations on Drawings to show where each insulation type is required.

Polyisocyanurate Board, Foil Faced <Insert drawing designation>: ASTM C 1289, foil faced, Type I, Class 1 or 2.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Fire Propagation Characteristics" Subparagraph below if required. Tested products are not available from all manufacturers for all types of assemblies.

Fire Propagation Characteristics: Passes NFPA 285 testing as part of an approved assembly.

GLASS-FIBER BLANKET

Retain "Sustainability Requirements" Paragraph below if required. Glass-fiber blanket insulation free of formaldehyde is available only from some manufacturers; other manufacturers produce low-emitting insulation certified by the Greenguard Environmental Institute.

Sustainability Requirements: Provide glass-fiber blanket insulation as follows:

Retain either "Free of Formaldehyde" or one of two "Low Emitting" subparagraphs below to suit Project.

Free of Formaldehyde: Insulation manufactured with 100 percent acrylic binders and no formaldehyde.

Low Emitting: Insulation tested according to ASTM D 5116 and shown to emit less than 0.05-ppm formaldehyde.

Retain "Low Emitting" Subparagraph below if required for LEED for Schools Credit IEQ 4.6.

Low Emitting: Complies with the testing and product requirements of the California Department of Public Health's (formerly, the California Department of Health Services') "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Retain "Recycled Content of Insulation" Paragraph below to specify recycled content if applying for LEED Credit MR 4. An alternative method of dealing with these credit requirements is to retain requirement in Section 018113.13 "Sustainable Design Requirements - LEED for New Construction and Major Renovations," Section 018113.16 "Sustainable Design Requirements - LEED for Commercial Interiors," or Section 018113.19 "Sustainable Design Requirements - LEED for Core and Shell Development" that gives Contractor the option and responsibility to determine how these credit requirements will be met.

Recycled Content of Insulation: Postconsumer recycled content plus one-half of preconsumer recycled content not less than <Insert number> percent.

Copy paragraphs below and re-edit for each type of insulation required. Insert drawing designations to identify each product. Use these designations on Drawings to show where each insulation type is required.

Glass-Fiber Blanket, Unfaced <Insert drawing designation>: ASTM C 665, Type I; with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84; passing ASTM E 136 for combustion characteristics.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Blanket, Polypropylene-Scrim-Kraft Faced <Insert drawing designation>: ASTM C 665, Type II (nonreflective faced), Class A (faced surface with a flame-spread index of 25 or less); Category 1 (membrane is a vapor barrier).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Blanket, Kraft Faced <Insert drawing designation>: ASTM C 665, Type II (nonreflective faced), Class C (faced surface not rated for flame propagation); Category 1 (membrane is a vapor barrier).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Blanket, Reinforced-Foil Faced <Insert drawing designation>: ASTM C 665, Type III (reflective faced), Class A (faced surface with a flame-spread index of 25 or less); Category 1 (membrane is a vapor barrier), faced with foil scrim, foil-scrim kraft, or foil-scrim polyethylene.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Blanket, Foil Faced <Insert drawing designation>: ASTM C 665, Type III (reflective faced), Class B (faced surface with a flame-propagation resistance of 0.12 W/sq. cm); Category 1 (membrane is a vapor barrier), faced with foil scrim, foil-scrim kraft, or foil-scrim polyethylene.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

GLASS-FIBER BOARD

Retain "Sustainability Requirements" Paragraph below if required. Glass-fiber board insulation free of formaldehyde is available only from some manufacturers; other manufacturers produce low-emitting insulation certified by the Greenguard Environmental Institute.

Sustainability Requirements: Provide glass-fiber board insulation as follows:

Retain either "Free of Formaldehyde" or one of two "Low Emitting" subparagraphs below to suit Project.

Free of Formaldehyde: Insulation manufactured with 100 percent acrylic binders and no formaldehyde.

Low Emitting: Insulation tested according to ASTM D 5116 and shown to emit less than 0.05-ppm formaldehyde.

Retain "Low Emitting" Subparagraph below if required for LEED for Schools Credit IEQ 4.6.

Low Emitting: Complies with the testing and product requirements of the California Department of Public Health's (formerly, the California Department of Health Services') "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Retain "Recycled Content of Insulation" Paragraph below to specify recycled content if applying for LEED Credit MR 4. An alternative method of dealing with these credit requirements is to retain requirement in Section 018113.13 "Sustainable Design Requirements - LEED for New Construction and Major Renovations," Section 018113.16 "Sustainable Design Requirements - LEED for Commercial Interiors," or Section 018113.19 "Sustainable Design Requirements - LEED for Core and Shell Development" that gives Contractor the option and responsibility to determine how these credit requirements will be met.

Recycled Content of Insulation: Postconsumer recycled content plus one-half of preconsumer recycled content not less than <Insert number> percent.

Copy paragraphs below and re-edit for each type of insulation required. Insert drawing designations to identify each product. Use these designations on Drawings to show where each insulation type is required.

Glass-Fiber Board, Unfaced <Insert drawing designation>: ASTM C 612, Type IA; unfaced, with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84[, passing ASTM E 136 for combustion characteristics]. Nominal density of 2.25 lb/cu. ft. (36 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Board, Faced <Insert drawing designation>: ASTM C 612, Type IA; faced on one side with foil-scrim-kraft or foil-scrim-polyethylene vapor retarder, with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84. Nominal density of 2.25 lb/cu. ft. (36 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Board, Unfaced <Insert drawing designation>: ASTM C 612, Type IA; unfaced, with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84[, passing ASTM E 136 for combustion characteristics]. Nominal density of 3 lb/cu. ft. (48 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Board, Faced <Insert drawing designation>: ASTM C 612, Type IA; faced on one side with foil-scrim-kraft or foil-scrim-polyethylene vapor retarder, with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84. Nominal density of 3 lb/cu. ft. (48 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Board, Unfaced <Insert drawing designation>: ASTM C 612, Type IA; unfaced, with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84[, passing ASTM E 136 for combustion characteristics]. Nominal density of 4.25 lb/cu. ft. (68 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Board, Faced <Insert drawing designation>: ASTM C 612, Type IA; faced on one side with foil-scrim-kraft or foil-scrim-polyethylene vapor retarder, with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84. Nominal density of 4.25 lb/cu. ft. (68 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Board, Unfaced <Insert drawing designation>: ASTM C 612, Type IA; unfaced, with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84[, passing ASTM E 136 for combustion characteristics]. Nominal density of 6 lb/cu. ft. (96 kg/cu. m), thermal resistivity of 4.4 deg F x h x sq. ft./Btu x in. at 75 deg F (30.5 K x m/W at 24 deg C).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Glass-Fiber Board, Faced <Insert drawing designation>: ASTM C 612, Type IA; faced on one side with foil-scrim-kraft or foil-scrim-polyethylene vapor retarder, with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84. Nominal density of 6 lb/cu. ft. (96 kg/cu. m), thermal resistivity of not less than 4.34 deg F x h x sq. ft./Btu x in. at 75 deg F (30.1 K x m/W at 24 deg C).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

MINERAL-WOOL BLANKETS

Retain "Recycled Content of Insulation" Paragraph below to specify recycled content if applying for LEED Credit MR 4. An alternative method of dealing with these credit requirements is to retain requirement in Section 018113.13 "Sustainable Design Requirements - LEED for New Construction and Major Renovations," Section 018113.16 "Sustainable Design Requirements - LEED for Commercial Interiors," or Section 018113.19 "Sustainable Design Requirements - LEED for Core and Shell Development" that gives Contractor the option and responsibility to determine how these credit requirements will be met.

Recycled Content of Insulation: Postconsumer recycled content plus one-half of preconsumer recycled content not less than <Insert number> percent.

Copy paragraphs below and re-edit for each type of insulation required. Insert drawing designations to identify each product. Use these designations on Drawings to show where each insulation type is required.

Mineral-Wool Blanket, Unfaced <Insert drawing designation>: ASTM C 665, Type I (blankets without membrane facing); consisting of fibers; with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, per ASTM E 84; passing ASTM E 136 for combustion characteristics.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Mineral-Wool Blanket, Reinforced-Foil Faced <Insert drawing designation>: ASTM C 665, Type III (reflective faced), Class A (faced surface with a flame-spread index of 25 or less per ASTM E 84); Category 1 (membrane is a vapor barrier), faced with foil scrim, foil-scrim kraft, or foil-scrim polyethylene.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

MINERAL-WOOL BOARD

Retain "Recycled Content of Insulation" Paragraph below to specify recycled content if applying for LEED Credit MR 4. An alternative method of dealing with these credit requirements is to retain requirement in Section 018113.13 "Sustainable Design Requirements - LEED for New Construction and Major Renovations," Section 018113.16 "Sustainable Design Requirements - LEED for Commercial Interiors," or Section 018113.19 "Sustainable Design Requirements - LEED for Core and Shell Development" that gives Contractor the option and responsibility to determine how these credit requirements will be met.

Recycled Content of Insulation: Postconsumer recycled content plus one-half of preconsumer recycled content not less than <Insert number> percent.

Copy paragraphs below and re-edit for each type of insulation required. Insert drawing designations to identify each product. Use these designations on Drawings to show where each insulation type is required.

Mineral-Wool Board, Types IA and IB <Insert drawing designation>: ASTM C 612, Types IA and IB; [unfaced,] [foil faced,] with maximum flame-spread and smoke-developed indexes of 15 and zero, respectively, per ASTM E 84; passing ASTM E 136 for combustion characteristics. Nominal density of 4 lb/cu. ft. (64 kg/cu. m).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Mineral-Wool Board, Type II <Insert drawing designation>: ASTM C 612, Type II; [unfaced,] [foil faced,] with maximum flame-spread and smoke-developed indexes of 15 and zero, respectively, per ASTM E 84; passing ASTM E 136 for combustion characteristics. Nominal density of 6 lb/cu. ft. (96 kg/cu. m).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Mineral-Wool Board, Type III <Insert drawing designation>: ASTM C 612, Type III; [unfaced,] [foil faced,] with maximum flame-spread and smoke-developed indexes of 15 and zero, respectively, per ASTM E 84; passing ASTM E 136 for combustion characteristics. Nominal density of 8 lb/cu. ft. (128 kg/cu. m).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

ACCESSORIES

Retain "Insulation for Miscellaneous Voids" Paragraph below for miscellaneous voids if needed for thermal protection or air-infiltration reduction.

Insulation for Miscellaneous Voids:

Glass-Fiber Insulation: ASTM C 764, Type II, loose fill; with maximum flame-spread and smoke-developed indexes of 5, per ASTM E 84.

Spray Polyurethane Foam Insulation: ASTM C 1029, Type II, closed cell, with maximum flame-spread and smoke-developed indexes of 75 and 450, respectively, per ASTM E 84.

Insulation Anchors, Spindles, and Standoffs: As recommended by manufacturer.

Retain "Adhesive for Bonding Insulation" Paragraph below for insulation adhesively bonded to substrates.

Adhesive for Bonding Insulation: Product compatible with insulation and air and water barrier materials, and with demonstrated capability to bond insulation securely to substrates without damaging insulation and substrates.

Retain "Eave Ventilation Troughs" Paragraph below if required for vented eaves in attics to receive blanket insulation.

Eave Ventilation Troughs: Preformed, rigid fiberboard or plastic sheets designed and sized to fit between roof framing members and to provide ventilation between insulated attic spaces and vented eaves.

EXECUTION

INSTALLATION, GENERAL

Comply with insulation manufacturer's written instructions applicable to products and applications.

Install insulation that is undamaged, dry, and unsoiled and that has not been left exposed to ice, rain, or snow at any time.

Extend insulation to envelop entire area to be insulated. Fit tightly around obstructions and fill voids with insulation. Remove projections that interfere with placement.

Provide sizes to fit applications and selected from manufacturer's standard thicknesses, widths, and lengths. Apply single layer of insulation units unless multiple layers are otherwise shown or required to make up total thickness or to achieve R-value.

INSTALLATION OF SLAB INSULATION

On vertical slab edge and foundation surfaces, set insulation units using manufacturer's recommended adhesive according to manufacturer's written instructions.

If not otherwise indicated, extend insulation a minimum of [24 inches (610 mm)] [36 inches (915 mm)] <Insert dimension> below exterior grade line.

On horizontal surfaces, loosely lay insulation units according to manufacturer's written instructions. Stagger end joints and tightly abut insulation units.

If not otherwise indicated, extend insulation a minimum of [24 inches (610 mm)] [36 inches (915 mm)] <Insert dimension> in from exterior walls.

INSTALLATION OF FOUNDATION WALL INSULATION

Verify, with manufacturer, methods of installation of insulation for concrete substrates. Revise paragraph below to indicate type of concrete substrate, such as architectural precast concrete panels or cast-in-place concrete walls. Revise to include channels for exposed insulation if required.

Butt panels together for tight fit.

Retain either "Anchor Installation" or "Adhesive Installation" Paragraph below to suit Project.

Anchor Installation: Install board insulation on concrete substrates by adhesively attached, spindle-type insulation anchors.

Adhesive Installation: Install with adhesive or press into tacky waterproofing or dampproofing according to manufacturer's written instructions.

INSTALLATION OF CAVITY-WALL INSULATION

Foam-Plastic Board Insulation: Install pads of adhesive spaced approximately 24 inches (610 mm) o.c. both ways on inside face and as recommended by manufacturer. Fit courses of insulation between wall ties and other obstructions, with edges butted tightly in both directions. Press units firmly against inside substrates.

Retain subparagraph below if insulation does not fill cavity. Coordinate with Section 042000 "Unit Masonry" where ties are specified.

Supplement adhesive attachment of insulation by securing boards with two-piece wall ties designed for this purpose and specified in Section 042000 "Unit Masonry."

INSTALLATION OF INSULATION IN FRAMED CONSTRUCTION

Blanket Insulation: Install in cavities formed by framing members according to the following requirements:

Use insulation widths and lengths that fill the cavities formed by framing members. If more than one length is required to fill the cavities, provide lengths that will produce a snug fit between ends.

Place insulation in cavities formed by framing members to produce a friction fit between edges of insulation and adjoining framing members.

Maintain 3-inch (76-mm) clearance of insulation around recessed lighting fixtures not rated for or protected from contact with insulation.

Retain first subparagraph below for eave ventilation.

Attics: Install eave ventilation troughs between roof framing members in insulated attic spaces at vented eaves.

Retain first subparagraph below for metal-framed construction.

For metal-framed wall cavities where cavity heights exceed 96 inches (2438 mm), support unfaced blankets mechanically and support faced blankets by taping flanges of insulation to flanges of metal studs.

Retain first subparagraph below for wood-framed construction.

For wood-framed construction, install blankets according to ASTM C 1320 and as follows:

With faced blankets having stapling flanges, lap blanket flange over flange of adjacent blanket to maintain continuity of vapor retarder once finish material is installed over it.

Vapor-Retarder-Faced Blankets: Tape joints and ruptures in vapor-retarder facings, and seal each continuous area of insulation to ensure airtight installation.

Specify location of vapor retarder in "Exterior Walls" Subparagraph below based on vapor-flow analysis of a construction assembly.

Exterior Walls: Set units with facing placed toward [exterior of construction] [interior of construction] [as indicated on Drawings].

Retain "Interior Walls" Subparagraph below for interior walls around high-humidity areas such as shower rooms and swimming pools.

Interior Walls: Set units with facing placed [as indicated on Drawings] [toward areas of high humidity] <Insert location>.

Miscellaneous Voids: Install insulation in miscellaneous voids and cavity spaces where required to prevent gaps in insulation using the following materials:

Glass-Fiber Insulation: Compact to approximately 40 percent of normal maximum volume equaling a density of approximately 2.5 lb/cu. ft. (40 kg/cu. m).

Spray Polyurethane Insulation: Apply according to manufacturer's written instructions.

INSTALLATION OF CURTAIN-WALL INSULATION

Install board insulation in curtain-wall construction according to curtain-wall manufacturer's written instructions.

Show width of cavity on Drawings.

Hold insulation in place by securing metal clips and straps or integral pockets within window frames, spaced at intervals recommended in writing by insulation manufacturer to hold insulation securely in place without touching spandrel glass. Maintain cavity width of dimension indicated on Drawings between insulation and glass.

Install insulation to fit snugly without bowing.

END OF SECTION 072100