## BJC
2018 BJC Lighting Standards Issued: February 1, 2018
(MTG) MOUNTING: |  | (Type) | LAMP TECHNOLOGY: | [5 empty] | (L/L) | LENS/LOUVER: |  |  | The goal of this base luminaire standard and selection table is to provide a starting point for the Lighting Designer. It is the responsibility of the design team to layout, calculate, validate selection and determine final acceptable design with the Owner and Authorities Having Jurisdiction. Substitution only permitted with written acceptance of there Director of Design or Corporate Engineer.
RE - | RECESSED | FL - | FLUORESCENT | [5 empty] | A- | .125" ACRYLIC
SP - | SUSPENDED | LED - | LIGHT EMITTING DIODE | [5 empty] | B- | BLACK BAFFLE
CL - | CEILING SURFACE | [7 empty] | C- | CLEAR ALZAK
WL - | WALL | [7 empty] | D- | PARABOLIC
UC - | UNDER CABINET | [7 empty] | F- | FRESNEL
CV - | COVE | [7 empty] | G- | TEMPERED GLASS
PL - | POLE | [7 empty] | H- | WALL WASHER
FR- | FLANGED RECESSED | [7 empty] | P- | POLY CARBONATE
O - | OTHER ( SEE DESCRIPTION) | [7 empty] | K- | KSH12 .125" ACRYLIC
DOOR: | [8 empty] | K19- | KSH19 .156" ACRYLIC
FA - | FLAT ALUMINUM | [7 empty] | L- | LOW IRIDESCENT SPECULAR ALUM.
FS - | FLAT STEEL | [7 empty] | N- | NONE
RA - | REGRESSED ALUMINUM | [7 empty] | R- | HIGH IMPACT DR ACRYLIC
RS - | REGRESSED STEEL | [7 empty] | O- | OTHER (SEE DESCRIPTION)
|  | (TYPE) | BALLAST:
FINISH: |  | DIM 02- 1% DIMMING DRIVER
PAF - | PAINT AFTER FABRICATION | DIM10- | 10% DIMMING DRIVER
CSA - | FINISH SELECTION BY ARCHITECT | EM- | EMERGENCY BATTERY/BALLAST
|  | MV- | MULTI-VOLTAGE ELECTRONIC 120V-277V
CATALOG NUMBER SHALL NOT BE CONSIDERED COMPLETE AND MATERIAL SHALL NOT BE ORDERED BY MANUFACTURER AND CATALOG NUMBER ONLY. THE COMPLETE DESCRIPTION AND THE SPECIFICATION SHALL BE COORDINATED WITH THE CATALOG NUMBER TO DETERMINE THE EXACT MATERIAL AND ACCESSORIES TO BE ORDERED. THE FIRST MANUFACTURER LISTED IS THE BASIS FOR DESIGN. SPECIFICATION SHOULD CLEARLY STATE CONTRACTOR RESPONSIBILITY FOR COORDIATION AND SUBMITTAL REGARDLESS OF OFCI DIRECTED. OFCI DIRECTED LIGHTING WILL BE INCLUSIVE TO LIGHT FIXTURES, LAMPS AND ACCESSORY CLIPS. CONTROLS ARE NOT INCLUDED IN ANY OFCI STRATEGY. DRAWING SCHEDULE SHALL INCLUDE QUANTITY TOTALING THE ENTIRE PROJECT.
LED LAMP CORRELATED COLOR TEMPERATURE 4000°K, COLOR RENDERING INDEX (CRI) AT OR ABOVE 80 FOR INTERIOR APPLICATIONS.
Fixture | DESCRIPTION | DIMENSIONS |  |  |  |  | LAMPS |  | DRIVER |  | L/L |  | LOCATION - FOOT CANDLE LEVEL (FC)
|  | L | W | H | DIA | MTG | TYPE | MODEL | VOLTS | TYPE
F1 | RECESSED DIRECT WITH HIGH ANGLE ILLUMINANCE, SMOOTH FROSTED ACRYLIC DIFFUSER, ONE LAMP CHAMBER. | 48" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX CRUZ 24CZ-LD5-**-S-UNV-L840-CD1-U / (4) EQ-CLIP-U (4000 - 5000 LUMENS) | HUDDLE ROOM - 30FC ADMIN AREA - 40FC CENTRAL CONTROL ROOM - 40FC OFFICE - 30FC SHARED LOUNGE - 30FC WORK ROOM - 50FC PROVIDER LOUNGE - 40FC BREAK ROOM - 30FC LARGE CONF ROOM - 50FC EXAM ROOM - 50FC ED VERTICAL BAY - 30FC TRIAGE - 40FC
F1A | RECESSED FLAT PANEL | 48" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 24FP**40C / FPEQ (4800 LUMENS) | HUDDLE ROOM - 30FC ADMIN AREA - 40FC CENTRAL CONTROL ROOM - 40FC OFFICE - 30FC SHARED LOUNGE - 30FC WORK ROOM - 50FC PROVIDER LOUNGE - 40FC BREAK ROOM - 30FC LARGE CONF ROOM - 50FC EXAM ROOM - 50FC ED VERTICAL BAY - 30FC TRIAGE - 40FC
F2 | RECESSED DIRECT WITH HIGH ANGLE ILLUMINANCE, SMOOTH FROSTED ACRYLIC DIFFUSER, ONE LAMP CHAMBER. PROVIDE WITH 1 TO 100 PERCENT DRIVER. | 48" | 24" | 3.25" |  | RE | LED |  | MV | DIM02 | O | METALUX CRUZ 24CZ-LD5-**-S-UNV-L840-HCD1-U / (4) EQ-CLIP-U (5500 - 6500 LUMENS) | PRE/POST & PACU BAY - 80FC INJECTION BAY - 100FC
F2A | RECESSED FLAT PANEL | 48" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 24FP**40C / FPEQ (6600 LUMENS) | PRE/POST & PACU BAY - 80FC INJECTION BAY - 100FC
F3 | STATIC GRID TROFFER WITH PRISMATIC LENS | 48" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX GRLED 24GR-LD5-**-F1-UNV-L840-CD1-U / (4) EQ-CLIP-U (3800 - 4800 LUMENS) | BREAK ROOM - 30FC STORAGE ROOM - 20FC MAIL ROOM - 30FC RECEIVING/BREAKDOWN AREA - 40FC RECEIVING WORKSTATION AREA - 30FC LAUNDRY ROOM - 20FC HOUSEKEEPING EQUIPMENT ROOM - 30FC CLEAN LINEN HOLDING - 30FC RODI ROOM - 30FC IT OFFICE - 30FC SOILED UTILITY ROOM - 25FC SCOPE ROOM - 50FC MED ROOM - 50FC LOCKER ROOM - 30FC LAB SUITE - 50FC SERVERY PREP AREA - 50FC FACILITY SHOP - 50FC BIO-MED ROOM - 50FC
F3A | RECESSED FLAT PANEL | 48" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 24FP**40C / FPEQ (4800 LUMENS) | BREAK ROOM - 30FC STORAGE ROOM - 20FC MAIL ROOM - 30FC RECEIVING/BREAKDOWN AREA - 40FC RECEIVING WORKSTATION AREA - 30FC LAUNDRY ROOM - 20FC HOUSEKEEPING EQUIPMENT ROOM - 30FC CLEAN LINEN HOLDING - 30FC RODI ROOM - 30FC IT OFFICE - 30FC SOILED UTILITY ROOM - 25FC SCOPE ROOM - 50FC MED ROOM - 50FC LOCKER ROOM - 30FC LAB SUITE - 50FC SERVERY PREP AREA - 50FC FACILITY SHOP - 50FC BIO-MED ROOM - 50FC
F4 | STATIC GRID TROFFER WITH PRISMATIC LENS | 24" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX GRLED 22GR-LD5-**-F1-UNV-L840-CD1-U / (4) EQ-CLIP-U (2400 - 3200 LUMENS) | TRASH CART HOLDING ROOM - 10FC B2 LOCKER ROOM - 20FC HOUSEKEEPING CLOSET/EVS ROOM - 20FC B2 CORRIDOR - 20FC B2 LOCKER ROOM - 20FC
F4A | RECESSED FLAT PANEL | 24" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 22FP**40C/FPEQ (2400 & 3500 LUMENS) | TRASH CART HOLDING ROOM - 10FC B2 LOCKER ROOM - 20FC HOUSEKEEPING CLOSET/EVS ROOM - 20FC B2 CORRIDOR - 20FC B2 LOCKER ROOM - 20FC
F5 | STATIC GRID TROFFER WITH PRISMATIC LENS, FLAT ALUMINUM DOOR, & "G3" GASKETING. PROVIDE WITH DRYWALL FRAME KIT. | 24" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX GRLED 22GRFA-LD5-**-F1-UNV-L840-CD1-G3-U / DF-22W-U (2400 - 3200 LUMENS) | PHARMACY - 60FC
F6 | 48" NARROW CHANNEL STRIP | 48" | 4" | 5" |  | SP | LED |  | MV | DIM10 | O | METALUX 4SNLED-LD5-**-**-UNV-L840-CD1-U / AYC-CHAIN/SET-U (2400 - 4700 LUMENS) | ELEC/MECH/ELEVATOR EQUIPMENT ROOM - 20FC TECHNOLOGY ROOM - 30FC BED REPAIR ROOM - 30FC MED GAS MANIFOLD ROOM - 10FC CHUTE ROOM - 20FC BIO-HAZARD HOLDING - 20FC PHARMACY WASTE ROOM - 20FC BODY HOLDING ROOM - 20FC SOILED LINEN HOLDING ROOM - 20FC SHELL SPACE - 10FC CHILLER PLANT - N/A
F7 | RECESSED DIRECT WITH HIGH ANGLE ILLUMINANCE, SMOOTH FROSTED ACRYLIC DIFFUSER, ONE LAMP CHAMBER. | 24" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX CRUZE 22CZ-LD5-**-S-UNV-L840-CD1-U / (4) EQ-CLIP-U (2000 - 3900 LUMENS) | STAFF LOUNGE - 30FC DEDICATED OFFICE - 40FC SHARED OFFICE - 40FC SMALL CONFERENCE ROOM - 50FC CORRIDOR - 20FC CPAP - 60FC LAB PROCESSING - 60FC
F7A | RECESSED FLAT PANEL | 24" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 22FP**40C / FPEQ (2400 & 3500 LUMENS) | STAFF LOUNGE - 30FC DEDICATED OFFICE - 40FC SHARED OFFICE - 40FC SMALL CONFERENCE ROOM - 50FC CORRIDOR - 20FC CPAP - 60FC LAB PROCESSING - 60FC
F8 | 6" APERTURE LED OPEN DOWNLIGHT, IP66 RATED, WHITE FINISH INCLUDING FLANGE. |  |  | 7" | 6" | RE | LED |  | MV | DIM02 | O | HALO COMMERCIAL PD6**D010B-PDM6B940-61VW (1000 - 1500 LUMENS) | ICU PATIENT TOILET ROOM - 30FC SHOWER - 20FC MULTI-STALL TOILET ROOM - 15FC ON-CALL ROOM - 30FC ENDO PROCEDURE ROOM - N/A ISOLATION BAY - N/A SCRUB SINK - 100FC OPERATING ROOM - N/A IR SUITE - N/A IMAGING ROOM - 50FC READING ROOM - 30FC ULTRASOUND ROOM - 40FC
F9 | SEMI-RECESSED AMBER STEPLIGHT, MATTE WHITE FINISH. | 6.1" | 4.85" | 3" |  | RE | LED |  | MV |  | O | KENALL MEDMASTER SOFTSTEP CONTOUR (SPECIFY STYLE) | NIGHTLIGHT - N/A
F10 | SEMI-RECESSED WHITE STEPLIGHT, RECTANGLE VERTICAL, INTERNAL LOUVER, 18-GAUGE CRS FACEPLATE, MATTE WHITE FINISH, CLEAR POLYCARBONATE LENS, PHILLIPS-HEAD FASTENERS. | 6.1" | 4.85" | 3" |  | RE | LED |  | MV |  | O | KENALL MEDMASTER SOFTSTEP STEPLIGHTS MSL | NIGHTLIGHT - N/A
F11 | 6" APERTURE MRI LED OPEN DOWNLIGHT, FLAT WHITE TRIM, LOW-GLOSS WHITE REFLECTOR, 0.125" CLEAR ACRYLIC LENS. |  |  | 6.38" | 8.63" | RE | LED |  |  | DIM02 | O | KENALL MEDMASTER RIMRI6-R-**-24V-DIM1 / MRIDL6-R-DCFW-**-40K8-M-CS-T *REQUIRES A REMOTE "MRIPS-312" POWER SUPPLY (MAX 8 FIXTURES PER ROOM / PER POWER SUPPLY | MRI ROOM - 50FC
F12 | RECESSED DIRECT WITH HIGH ANGLE ILLUMINANCE, FLAT MATTE ACRYLIC DIFFUSER, SINGLE LAMP CHAMBER. PROVIDE 20-GAUGE CRS HOUSING AND SYMMETRIC OPTICS. | 48" | 24" | 4.5" |  | RE | LED |  |  | DIM02 | O | KENALL MEDMASTER M4SEDI24-**-40K8-DCC-XXX-2F-2H-SYM (11,000 - 13,900 LUMENS) | OPERATING ROOM - 200FC
F12E | SAME AS F12 EXCEPT PROVIDED WITH INTERGRAL EMERGENCY BATTERY PACK. (NOTE: BATTERY PACK INCREASES OVERALL HEIGHT OF FIXTURE TO 8.75") | 48" | 24" | 8.75" |  | RE | LED |  |  | DIM02 / EM | O | KENALL MEDMASTER M4SEDI24-**-40K8-DCC-XXX-2F-2H-SYM-LEL (11,000 - 13,900 LUMENS) | OPERATING ROOM - 200FC
F13 | RECESSED DIRECT WITH HIGH ANGLE ILLUMINANCE, FLAT MATTE ACRYLIC DIFFUSER, SINGLE LAMP CHAMBER. PROVIDE 20-GAUGE CRS HOUSING AND SYMMETRIC OPTICS. | 24" | 24" | 4.5" |  | RE | LED |  | MV | DIM02 | O | KENALL MEDMASTER M4SEDI22-***-40K8-DCC-XXX-2F-2H-SYM (10,000 - 13,0000 LUMENS) | OPERATING ROOM - 200FC
F14 | RECESSED DIRECT WITH HIGH ANGLE ILLUMINANCE, SMOOTH FROSTED ACRYLIC DIFFUSER, ONE LAMP CHAMBER. | 48" | 12" | 5.5" |  | RE | LED |  | MV | DIM10 | O | METALUX CRUZE 14CZ-LD5-**-S-UNV-L840-CD1-U / (4) EQ-CLIP-U (2000 - 3500 LUMENS) | PRE/POST PATIENT CARE STATION - 30FC ED GREETER DESK - 40FC CARDIOLOGY ROOM - 50FC
F14A | RECESSED FLAT PANEL | 48" | 12" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 14FP**40C (4300 LUMENS) | PRE/POST PATIENT CARE STATION - 30FC ED GREETER DESK - 40FC CARDIOLOGY ROOM - 50FC
F15 | PATIENT BED LIGHT WITH AMBIENT, EXAM, & READER LIGHT. INCLUDE LOW VOLTAGE LIGHTING CONTROL RELAY | 48" | 8" | 5.25 |  | RE | LED |  | MV | DIM02 / ML | O | FOCAL POINT APOLLO FMA8LR-84-RA-**-40K-**-30K-**-35K-3C-***-L11-G-WHA | ISOLATION BAY - 80FC ICU - 80FC ACUTE PATIENT ROOM - 80FC
F16 | GASKETED STATIC GRID TROFFER WITH PRISMATIC LENS, ALUMINUM DOOR FRAME. | 48" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX GRLED 24GRFA-LD5-**-F1-UNV-L840-CD1-G3-U / (4) EQ-CLIP-U (3400 - 4800 LUMENS) | CSPD:SUPPLY STORAGE AREA - 75FC CSPD:SCOPE PROCESSING CLEAN ROOM - 50FC CSPD:SCOPE PROCESSING SOILED ROOM - 75FC OR EQUIPMENT SUPPLIES ROOM - 30FC OR FLEX ROOM - 50FC KITCHEN - 60FC ED DECONTAM ROOM - 40FC PHARMACY - 60FC
F16A | RECESSED FLAT PANEL | 48" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 24FP**40C / FPEQ (4800 LUMENS) | CSPD:SUPPLY STORAGE AREA - 75FC CSPD:SCOPE PROCESSING CLEAN ROOM - 50FC CSPD:SCOPE PROCESSING SOILED ROOM - 75FC OR EQUIPMENT SUPPLIES ROOM - 30FC OR FLEX ROOM - 50FC KITCHEN - 60FC ED DECONTAM ROOM - 40FC
F17 | GASKETED STATIC GRID TROFFER WITH PRISMATIC LENS, ALUMINUM DOOR FRAME | 48" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX GRLED 24GRFA-LD5-**-F1-UNV-L840-CD1-G3-U / (4) EQ-CLIP-U (7200 LUMENS) | CSPD:DECONTAM AREA - 120FC CSPD:ASSEMBLY AREA - 120FC OR CORRIDOR - 50FC
F17A | RECESSED FLAT PANEL | 48" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 24FP**40C / FPEQ (6600 LUMENS) | CSPD:DECONTAM AREA - 120FC CSPD:ASSEMBLY AREA - 120FC OR CORRIDOR - 50FC
F18 | GASKETED STATIC GRID TROFFER WITH PRISMATIC LENS | 24" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX GRLED 22GRFA-LD5-**-F1-UNV-L840-CD1-G3-U / (4) EQ-CLIP-U (4300 LUMENS) | ENDO PROCEDURE ROOM - 50FC IR SUITE - 50FC
F18A | RECESSED FLAT PANEL | 24" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 22FP**40C / FPEQ (3500 LUMENS) | ENDO PROCEDURE ROOM - 50FC IR SUITE - 50FC
F19 | 4" APERTURE LED OPEN DOWNLIGHT, SPECULAR CLEAR REFLECTOR WITH WHITE RING. |  |  | 5.5" | 4.5" | RE | LED |  | MV | DIM10 | O | COOPER HALO H457TATE010-EL406940-TL410SC | ELEVATOR LOBBY - N/A
F20 | LED VANITY FIXTURE ***ONLY USE IF ABSOLUTELY NECESSARY*** | 25.25" | 4" | 5" |  | WL | LED |  | MV |  | O | AFX ALV ALV2505**30SND2 | STAFF/PATIENT TOILET ROOM - 20FC
F21 | PARKING GARAGE LUMINAIRE, SURFACE MOUNT. DIE-CAST ALUMINUM HOUSING. INJECTION MOLDED ACRYLIC LENS WITH VARYING DISTRIBUTIONS PER JOB. IP66 RATED |  |  | 4-7/8" | 18-3/8" | CL | LED |  | MV | DIM10 | O | MCGRAW-EDISON TOP TIER TT-**-LED-E1-**-** (5000 - 9600 LUMENS) | PARKING GARAGE - 9FC
F22 | EXTERIOR WALL PACK. MOUNT 8'-0" ABOVE FINISH GRADE OR DOCK FLOOR. | 6-3/4" | 3-5/8" | 5-3/4" |  | WL | LED |  | MV |  | O | EATON LUMARK XTOR XTOR**-W (2100 LUMENS) | EXTERIOR DOORS - 4FC
F23 | EXTERIOR WALL PACK WITH HI/LO DIMMING VIA INTEGRAL MOTION SENSOR AND REFRACTIVE LENS. MOUNT 10' ABOVE FINISHD GRADE. | 8-3/4" | 7" | 11" |  | WL | LED |  |  |  | O | EATON LUMARK XTOR XTOR**BRL-W-MS/DIM-L20 (1) FSIR-100-PK PER JOB (6000 - 8300 LUMENS) | PLANT YARD - 3FC
F23E | SAME AS F23 EXCEPT PROVIDED WITH EMERGENCY BATTERY PACK. | 8-3/4" | 7" | 11" |  | WL | LED |  |  | EM | O | EATON LUMARK XTOR XTOR**BRL-W-MS/DIM-L20-CBP (1) FSIR-100-PK PER JOB (6000 - 8300 LUMENS) | PLANT YARD/ELECTRICAL EQUIPMENT - 3FC
F24 | RECESSED LINEAR LED LUMINAIRE WITH FLUSH LENS | PER PLAN | 4" | 4.75" |  | RE | LED |  | MV | DIM10 | O | FOCAL POINT FSM4L-FL-**LF-40K-1C-UNV-LD1-**-WH-*PER FOOT* *OR* FINELITE HP-4 R-*PER FOOT*-**-840-F-VOLT-SC-** (375 - 1000 LUMENS PER FOOT) | ACUTE PATIENT TOILET ROOM - 40FC STAFF/PUBLIC TOILET ROOM - 30FC PROCEDURAL WAITING AREA - 25FC MAIN LOBBY/DINING AREA - 20FC SERVERY - 20FC ED WAITING AREA - 25FC IMAGING WAITING AREA - 25FC PUBLIC TOILET ROOM - 20FC STAFF SHOWER ROOM - 30FC CORRIDOR - 20FC ELEVATOR LOBBY - 20FC
F25-"IN USE" | WALL MOUNTED LED IN-USE SIGN. TEXT FOR IMAGING ROOMS SHALL READ: "IN-USE" | 12.25" | 2.25" | 7.5" |  | WL | LED |  | MV |  | O | COOPER SURE-LITES CX CX6SR5 | IN-USE SIGN - N/A
F25-"MAGNET ON" | WALL MOUNTED LED IN-USE SIGN. TEXT FOR MRI IMAGING ROOMS SHALL READ: "MAGNET ON" | 12.25" | 2.25" | 7.5" |  | WL | LED |  | MV |  | O | COOPER SURE-LITES CX CX6SR-MAGNET ON | MAGNET ON SIGN - N/A
F26 | WALL MOUNTED STAIRWELL LED STRIP WITH FROSTED LENS. WALL MOUNT +96" ABOVE STAIRWELL LANDING MEASURED FROM CENTERLINE OF LUMINAIRE. PROVIDED WITH SENSOR. | 48" | 4.5" | 4-11/16" |  | WL | LED |  | MV | DIM10 | O | METALUX SWLED 4SWLED-LD4-**-LW-UNV-L840-CD1-SVPD1-U (1) ISHH-01 PER JOB (2000 - 4000 LUMENS) | EGRESS STAIRWELL - 15FC
F27 | CEILING MOUNTED LED STRIP WITH FROSTED LENS. PROVIDED WITH SENSOR. | 48" | 4.5" | 4-11/16" |  | CL | LED |  | MV | DIM10 | O | METALUX SWLED 4SWLED-LD4-**-LW-UNV-L840-CD1-SVPD1-U (1) ISHH-01 PER JOB (2000 - 4000 LUMENS) | CORRIDOR - 20FC EXTERIOR FLAMMABLE STORAGE ROOM - 20FC
F28 | 96" NARROW CHANNEL STRIP. SUSPEND 8'-0" AFF UNLESS NOTED OTHERWISE ON THE PLANS. | 96" | 4" | 5" |  | SP | LED |  | MV | DIM10 | O | METALUX SNLED 8TSNLED-LD5-**-**-UNV-L840-CD1-U / AYC-CHAIN/SET-U (6200 - 8500 LUMENS) | MECH ROOM - 20FC DISASTER EQUIPMENT STORAGE ROOM - 20FC FIRE PUMP ROOM - 20FC STOCK MATERIAL STORAGE ROOM - 20FC SHELL SPACE - 10FC
F29 | 4' LED ENCLOSED VAPORTITE WALL MOUNTED OR SUSPENDED | 48" | 7" | 5-7/8" |  | WL/SP | LED |  | MV | DIM10 | O | METALUX VAPORTITE LED 4VT2-LD4-**-DR-W-UNV-L840-CD1-WL-U | ELEVATOR SHAFT - 10FC STERILIZERS EQUIPMENT ROOM - 20FC CART WASHER EQUIPMENT ROOM - 20FC
F30 | LINEAR LED FIXTURE, FLUSH SATIN LENS. WET LOCATION VERSION. FOR INSTALLATION IN GYPSUM CEILING | PER PLAN | 4" | 4.5" |  | RE | LED |  | MV | DIM10 | O | FOCAL POINT SEEM 4 WL FSM4LWL-FL-**-40K-1C-UNV-LD1-TF-WH-*PER FOOT* | CONCIERGE - 25FC MAIN ENTRY VESTIBULE - 15FC
F31 | VANDAL PROOF DIRECT AND INDIRECT LED FIXTURE. PROVIDE WITH STEEL DOOR AND TAMPERPROOF SCREWS. | 48" | 24" | 5" |  | RE | LED |  | MV | DIM10 | O | EATON FAIL-SAFE SGI LED SGI-G-4-LD4-**-40-CA125-FA-CRSW-UNV-EDD1-TP | ED EXAM ROOM - 50FC
F32 | LED COVE LIGHT. LENGTH AS NOTED ON PLANS. INTERIOR RATED. | PER PLAN | 2.4" | 1.4" |  | CV | LED |  | MV | DIM10 | O | LUMENPULSE LUMENCOVE NANO LCN2-HO-UL-VOLT-12"-40K-**-WH | INTERIOR COVE
F33 | LINEAR LED WALL WASH FIXTURE. PROVIDE CONTINUOUS LENGTH AS SHOWN ON PLANS. | PER PLAN | 1 1/2" | 3 3/4" | N/A | RE | LED |  | MV | DIM10 |  | LUMENWERX VIA 1.5 LED VIA1.5R-WRO-LED-80-**-40-PER FOOT-UNV-D-1-XX-W | L1 LARGE CONF ROOM STAGING AREA WALL WASHER - N/A
F34 | SHALLOW WALL GRAZER, CONTINOUS ROW, SOLID HOUSING, INTEGRAL ELECTRONIC DRIVER ANODIZED ALUMINUM FINISH. LENGTH AS SHOWN ON PLANS. | PER PLAN | 3" | 5" |  | RE | LED |  | MV | DIM10 | N | LUMENWERX VIA SKIM 3 LED V3SKIS-GRO-LED-80-**-40-PER FOOT-UNV-D1-1-XX | MAIN ENTRY WOOD WALL GLAZING - N/A ELEVATOR GLASS WALL GLAZING - N/A
S1 | PARKING LOT / SITE LIGHTING FIXTURE. EACH JOB'S POLE SPEC REQUIREMENT WILL BE DIFFERENT | 21.75" | VARIES | 4" |  | PL | LED |  | MV | DIM10 | O | MCGRAW-EDISON GALEON GLEON-AF-** | PARKING LOT - 4FC
X1 | SINGLE-FACE EXIT SIGN, WHITE DIE-CAST ALUMINUM BODY, RED LETTERS, UNIVERSAL ARROWS / MOUNTING. AC ONLY - NO BATTERY BACKUP | 11.5" | 2" | 9.5" |  | CL/ WL | LED | 3.5 WATT L.E.D. | MV |  | O | EATON SURE-LITES CX SERIES CX61WH | CORRIDORS - N/A
X2 | DOUBLE-FACE EXIT SIGN, WHITE DIE-CAST ALUMINUM BODY, RED LETTERS, UNIVERSAL ARROWS / MOUNTING. AC ONLY - NO BATTERY BACKUP | 11.5" | 2" | 9.5" |  | CL/ WL | LED | 3.5 WATT L.E.D. | MV |  | O | EATON SURE-LITES CX SERIES CX62WH | CORRIDORS - N/A
M1 | RECESSED DIRECT WITH HIGH ANGLE ILLUMINANCE, SMOOTH FROSTED ACRYLIC DIFFUSER, ONE LAMP CHAMBER. | 48" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX CRUZ 24CZ-LD5-**-S-UNV-L840-CD1-U / (4) EQ-CLIP-U (4000 - 5000 LUMENS) | MOB PATIENT & PUBLIC SPACE
M1A | RECESSED FLAT PANEL | 48" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 24FP**40C / FPEQ (4800 LUMENS) | MOB PATIENT & PUBLIC SPACE
M2 | RECESSED DIRECT WITH HIGH ANGLE ILLUMINANCE, SMOOTH FROSTED ACRYLIC DIFFUSER, ONE LAMP CHAMBER. | 24" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX CRUZE 22CZ-LD5-**-S-UNV-L840-CD1-U / (4) EQ-CLIP-U (2000 - 3900 LUMENS) | MOB PATIENT & PUBLIC SPACE MOB CORRIDOR - 20FC
M2A | RECESSED FLAT PANEL | 24" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 22FP**40C / FPEQ (2400 & 3500 LUMENS) | MOB PATIENT & PUBLIC SPACE
M3 | STATIC GRID TROFFER WITH PRISMATIC LENS | 48" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 | O | METALUX GRLED 24GR-LD5-**-F1-UNV-L840-CD1-U / (4) EQ-CLIP-U (3800 - 4800 LUMENS) | MOB SUPPORT SPACE & BACK OF HOUSE
M3A | RECESSED FLAT PANEL | 48" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 | O | METALUX FP 24FP**40C / FPEQ (4800 LUMENS) | MOB SUPPORT SPACE & BACK OF HOUSE
M4 | RECESSED DIRECT WITH HIGH ANGLE ILLUMINANCE, SMOOTH FROSTED ACRYLIC DIFFUSER, ONE LAMP CHAMBER. PROVIDED WITH EMERGENCY BATTERY BACKUP. | 24" | 24" | 3.25" |  | RE | LED |  | MV | DIM10 / EM | O | METALUX CRUZ 22CZ-LD5-**-S-UNV-EL14W-L840-CD1-U / (4) EQ-CLIP-U (2000 - 3900 LUMENS) | MOB EGRESS CORRIDOR - 4FC
M4A | RECESSED FLAT PANEL. PROVIDED WITH REMOTE MOUNTED EMERGENCY BATTERY BACKUP | 24" | 24" | 1.75" |  | RE | LED |  | MV | DIM10 / EM | O | METALUX FP 22FP**40C / EBPLED14W / FPEQ (2400 & 3500 LUMENS) | MOB EGRESS CORRIDOR - 4FC
M5 | 6" APERTURE LED OPEN DOWNLIGHT, IP66 RATED, WHITE FINISH INCLUDING FLANGE. |  |  | 7" | 6" | RE | LED |  | MV | DIM02 | O | HALO COMMERCIAL PD6**D010B-PDM6B940-61VW (1000 - 1500 LUMENS) | MOB PATIENT & PUBLIC SPACE MOB CORRIDOR - 20FC
M6 | 6" APERTURE LED OPEN DOWNLIGHT, IP66 RATED, WHITE FINISH INCLUDING FLANGE. PROVIDED WITH EMERGENCY BATTERY PACK. |  |  | 7" | 6" | RE | LED |  | MV | DIM02 / EM | O | HALO COMMERCIAL PD6**D010BIEM-PDM6B940-61VEW (1000 - 1500 LUMENS) | MOB MULTI-STALL TOILET ROOM EGRESS - 5FC
M7 | RECESSED LINEAR LED LUMINAIRE WITH FLUSH LENS | PER PLAN | 4" | 4.75" |  | RE | LED |  | MV | DIM10 | O | FOCAL POINT FSM4L-FL-**LF-40K-1C-UNV-LD1-**-WH-*PER FOOT* *OR* FINELITE HP-4 R-*PER FOOT*-**-840-F-VOLT-SC-** (375 - 1000 LUMENS PER FOOT) | MOB CORRIDOR - 20FC
M8 | WALL MOUNTED STAIRWELL LED STRIP WITH FROSTED LENS. WALL MOUNT +96" ABOVE STAIRWELL LANDING MEASURED FROM CENTERLINE OF LUMINAIRE. PROVIDED WITH EMERGENCY BATTERY BACKUP. | 48" | 4.5" | 4-11/16" |  | WL | LED |  | MV | DIM10 / EM | O | METALUX SWLED 4SWLED-LD4-**-LW-UNV-EL14W-L840-CD1-SVPD1-U (1) ISHH-01 PER JOB | MOB EGRESS STAIRWELL - 10FC
M9 | 96" NARROW CHANNEL STRIP. SUSPEND 8'-0" AFF UNLESS NOTED OTHERWISE ON THE PLANS. PROVIDED WITH EMERGENCY BATTERY BACKUP | 96" | 4" | 5" |  | SP | FL | 32W T8 | MV | EM | N | METALUX SNF 8TSNF-232-UNV-EL4LP-ER81-U / AYC-CHAIN/SET-U | MOB SHELL SPACE EGRESS - 8FC
M10 | LINEAR LED FIXTURE, FLUSH SATIN LENS. WET LOCATION VERSION. FOR INSTALLATION IN HARD SURFACE NON-DRYWALL CEILING | PER PLAN | 4" | 4.5" |  | RE | LED |  | MV | DIM10 | O | FOCAL POINT SEEM 4 WL FSM4LWL-FL-**-40K-1C-UNV-LD1-XFN-WH-*PER FOOT* | MOB ENTRY CANOPY - 2FC
MX | UNIVERSAL FACE EXIT SIGN, WHITE THERMOPLASTIC BODY, RED LETTERS, UNIVERSAL ARROWS / MOUNTING. BATTERY BACKUP INCLUDED | 11.7" | 1.7" | 7.2" |  | CL/ WL | LED | 1.2 WATT L.E.D. | MV |  | O | EATON SURE-LITES APX APX7R | MOB CORRIDORS - N/A

## IESNA
RECOMMENDED LIGHT LEVELS - IESNA 10th EDITION | [6 empty] | RECOMMENDED MAINTAINED FOOT-CANDLES (FC)
INTERIOR |  |  | HORIZ | VERT | Max/Min | CHAPTER |  | Notes
| Conference Rooms (Video Conference) |  | 30-50 | 30 | 3:1 | 22 | Common Applications 22.2
| Open Office (Intermittent Computer Use) |  | 30 | 15 | 3:1 | 22
| Classrooms (writing / VDT /AV) |  | 40/ 15 /5 | 15/ 5 /3 | 3:1 | 24 | 30 vertical of whiteboard, 15 vert on tackboard
| Corridors (day / night) |  | 10 / 5 | 5 / 2 | 3:1 | 27
| Art Rooms |  | 50 | 30 | 3:1 | 24 | Lighting for Education 24.2
| Science Labs, Kitchen (Demonstration / bench) |  | 100 / 50 | 50 / 30 | 3:1 | 24
| Lecture Halls (Demonstration / no AV / AV) |  | 100/ 10 /1 | 50/ 4 / 2 | 2:1 | 24
| Music Rooms |  | 30 | 20 | 2:1 | 24
| Library (general / reading) |  | 10 / 50 | 3 / 20 | 3:1 | 29
| Cafeterias |  | 15-30 | 3 | 3:1 | 22
| Gymnasiums (high school class II, college class II) |  | 50/80 | 30 | 3:1 2.5:1 | 24
| Shops |  | 50 | 25 | 3:1 | 24 | observers <25 years
| Lobby (DAY / NIGHT) |  | 30 / 15 | 15 / 7.5 | 3:1 | 22
| Offices |  | 30 - 50 | 15 | 3:1 | 22
| Toilets |  | 10 - 15 | 20 | 2:1 | 22 | 15 at vanity
| Mechanical / Electrical utility rooms |  | 20 / 10 | 15 / 10 | 3:1 | 22 | automatic shutoff not allowed without override
| Stairs |  | 10 | 5 | 2:1 | 22 | minimum on tread
| General Merchandise Display (department / drug) |  | 40 / 50 | 15 / 20 | 2:1/1.5:1 | 34 | Lighting for retail 34.2
| Feature Display |  |  |  |  | 34 | 10X / 5X / 1X adjacent retail level
| Retail circulation (department / drug) |  | 15 / 20 | 5 / 7.5 | 2:1 | 34
| Cardiac Function Lab (EEG) EXAM / GENERAL |  | 50 / 30 | 15 / 10 | 3:1 | 27 | Healthcare Facilities Illuminance IES 27.2
| Central Sterile Supply (inspection / clean) |  | 50 / 30 | 30 / 10 | 3:1 | 27
| Critical Care Areas (Exam) |  | 50 | 10 | 3:1 | 27
| Recovery (Exam / Observation / Rest) |  | 100/ 50 /10 | 30/ 20 /3 | 3:1 | 27
| Dialysis (insertion / chair / general) |  | 100/50/20 | 15 | 3:1 | 27
| Emergency (General / table) |  | 50/100 | 15/30 | 3:1 | 27
| Endoscopy |  | 50 | 15 | 3:1 | 27
| Lab (BENCHES / GENERAL) |  | 100 / 50 | 30 / 15 | 3:1 | 27
| Soiled/Clean Utility |  | 30 | 10 | 3:1 | 27
| Medical Records |  | 50 | 10 | 3:1 | 27
| Nurseries (General / Observation) |  | 10 / 30 | 3 / 5 | 4:1 | 27
| Nurse Station (Day / Night) Inpatient |  | 50 / 10 | 20 / 4 | 3:1 | 27 | Horizontal +0'AFF Veritcal +5' AFF
| LDRP (General) / night |  | 50 / 30 | 20 | 4:1 | 27
| Patient Rooms (Exam / general / reading) |  | 50/ 5 /20 | 20 | 3:1 / 4:1 | 27
| Physical Therapy (treatment / general) |  | 50 / 10 | 20 / 3 | 3:1 | 27
| Radiology (prep / procedure) |  | 50 / 5 | 15 / 2 | 3:1 / 4;1 | 27
| Operating Rooms (setup / general/table) |  | 100/200/300 | 50/75/100 | 4:1 / 2:1 | 27
| Waiting Areas (general / Reading / TV) |  | 4/ 30 /4 | 2/ 7.5 /2 | 3:1 | 27
| Storage Rooms |  | 10 | 3
General lighting should be 1/3 the intensity of task lighting. Contrast ratio should be 10:1 or less. Vertical is measured @ +4' UNO
RECOMMENDED FOOT-CANDLES (FC)
EXTERIOR |  |  | HORIZ | VERT | Max/Min | Avg/Min | CHAPTER
| BUILDING ENTRIES (Canopy / High / Med/ Low) |  | 4 / 2 / 1 | 2 / 1 / .6 | 4:1 | 2:1 | 22
| PEDESTRIAN MALLS (Hi / Med / Low Activity) |  | 0.8 / .6 / .4 | .4/.2 /.1 | 4:1 | 5:1 | 34
| PARKING LOT |  | 0.2 min | 0.1 | 20:1 |  |  | MINIMUM MAINTAINED, MAX-MIN
| PARKING LOT | ENHANCED SECURITY | 0.5 min | 0.25 | 15:1 |  |  | MINIMUM MAINTAINED, MAX-MIN
| PARKING RAMP | DAY | 2 min. | 1 | 10:1 |  |  | MINIMUM MAINTAINED, MAX-MIN
| PARKING RAMP | NIGHT | 1 minimum | 0.5 | 10:1 |  |  | MINIMUM MAINTAINED, MAX-MIN
| RAMP ENTRY | DAY / NIGHT | 50 / 1 |  | 10:1
| DRIVEWAY / LOCAL ROAD |  | 0.6 |  | 6 : 1
| WALKWAYS |  | .2 - .01 |  |  |  |  | MINIMUM MAINTAINED, MAX-MIN
EMERGENCY & EGRESS LIGHTING |  |  | RECOMMENDED FOOT-CANDLES (FC)
|  | 2009 NFPA 101 7.8.1.3 | HORIZ | VERT |  | Avg/Min
EGRESS PATH |  |  | 1 |  |  | 10:1 | MINIMUM .1 ftc along 3' band centered on egress path
Areas adjacent to EGRESS PATH |  |  | 0.05
STAIRWELLS |  | 10 ftc Normal | 1
EXTERIOR PATH OF EGRESS |  |  | 1 |  |  |  | To public way, or safe distance from exit discharge
Failure of 1 lamp shall not leave an area in total darkness <=.2 ftc |  |  |  | NFPA 101 7.8.1.4, NEC 700.16, IBC 1003.2.11, UBC 1006.1,
LIGHTING CALCULATIONS |  |  |  | Room Cavity Ratio (RCR) = |  |  |  | 5 * Working Cavity * (L+W)
| B.F. = Ballast factor | [6 empty] | Spare (Area)
L.L.F. = Lamp Lumen Depreciation * Dirt Depreciation
|  |  |  | Maintained Foot Candles (FC) = |  |  |  | #Lamps * Lumens * CU * LLF * BF
Spare (Area)
Note on A42: John McGonegle: