SECTION 23 52 39 – fire tube Boilers

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide [packaged,] [factory-fabricated] [and] [factory-fabricated and] [field] assembled, [gas] [oil] [combination gas- and oil]-fired, Lo NOx fire-tube boiler, with Lo Nox burner, trim, and accessories for generating steam.  The boiler shall operate with DDC microprocessor based controls that comply with ANSI/ASHRAE Standard 135, and shall include documents and supplementary items necessary to ensure proper installation and operation.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references and where noted within this Section:

ANSI/ASME Boilers and Pressure Vessel Code, Section VIII, Division 1 Design and Fabrication of Pressure Vessels.

ASME Compliance:  Fabricate and label cast-iron boilers in accordance with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

ASME SEC IV - Boiler and Pressure Vessels Code - Rules for Construction of Heating Boilers.

Comply with FM Global Standards.

Local Municipal Codes are applicable to the design and installation of boiler.

AGA Z21.13 - Gas-Fired Low-Pressure Steam and Hot Water Boilers.

Clean Air Act Amendments (Title’s I and IV).

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

For boilers that operate at more than 15 psig (104 kPa):

In conformance with ASHRAE, MBtu or Mbh, intended to mean 1000 Btu and 1000 Btu/hr MM, will indicate 1,000,000 or 106.

ASHRAE/IESNA 90.1 Compliance:  Condensing boilers shall have a minimum efficiency in accordance with ASHRAE Standard 90.1, Table 6.2.1F.

HI - Testing and Rating Standard for Cast Iron and Steel Heating Boilers.

NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

UL Compliance:  Test condensing boilers in accordance with UL 726, “Oil-Fired Boiler Assemblies.”

UL Compliance:  Test condensing boilers in accordance with UL 795, “Commercial-Industrial Gas Heating Equipment.”

The manufacturer shall test and inspect factory-assembled boilers, before shipping, in accordance with ASME Boiler and Pressure Vessel Code:  Section IV.

Burner and Hydrostatic Test:  The manufacturer shall factory adjust the burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen, and carbon monoxide in flue gas and set to achieve rated combustion efficiency; perform hydrostatic test.  Boiler shall be factory hydrostatically tested.

Owner shall be allowed access to observe first-hand the quality control testing of cast-iron boilers.  Owner shall be notified 14 calendar days in advance of testing.

SUBMITTALS

Product Data:

Shop Drawings shall indicate size, profiles, and dimensional requirements of condensing boilers and shall be based on the specific system indicated.

Include component sizes, capacities, rough-in requirements, service sizes and electrical connection requirements for boilers, boiler trim, and accessories.  Include plans, elevations, sections, and details.

Record Documents:

Submit Shop Drawings and product data with component sizes, capacities, rough-in requirements, service sizes and electrical connection requirements for boilers, boiler trim, and accessories.  Include plans, elevations, sections, details, and attachments to other Work.  Shop Drawings shall be signed and sealed by a qualified registered professional engineer.

Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails, and base weights.

Wiring Diagrams:  Detail power, signal, and control wiring.

Submit detail of gas train with all components clearly identified.

Operation and Maintenance Data:

Operation and maintenance data to include Operating and Maintenance Manuals.

Provide the following documents to be delivered to the Owner upon completion of Work.

Test Reports:

Factory Test.

Performance Test.

Certificates and Permits:

ASME “A” Stamp Certification and Report:  Submit “A” stamp certificate of authorization, and document hydrostatic testing of piping external to boiler.

Start-up service reports.

Construction and Operating Permits, as required by state of Missouri and regulations from Air Pollution Control Authorities.

Necessary Permit(s) from FM Global.

Warranties:  Special warranties specified in this Section.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

manufacturers

Owner Equipment Procurement Procedures.

Fire tube boilerS

Description:  Factory-fabricated, -assembled, and -tested fire-tube boiler with heat exchanger sealed pressure-tight, built on a steel base; including insulated jacket; flue-gas vent; combustion-air intake connections; water supply, return, and condensate drain connections; and controls.

[If the applicable Boiler capacity and performance data is indicated on the Drawings, then the following blank performance data in the following sub-sections can be excluded from this Specification.]

Boiler Characteristics and Capacities:

Heating Medium:  Steam.

Maximum Design Pressure Rating:  [150 psig.]

Maximum Design Pressure Rating:  [160 psig.]

Operating Pressure:  [___psig.]

Steam Flow Rate:  [___lb/h.]

Minimum Efficiency:  AFUE.

AGA Output Capacity: [___ Mbh.]

Fire-Tube Boiler Components:

Heat Exchanger:  Nonferrous, corrosion-resistant combustion chamber.

Pressure Vessel:  Carbon steel with welded heads and tube connections.

Burner:  Natural gas, forced draft.

AGA Input:  [___Mbh.]

Gas Input:  [___SCFH.]

Blower:  Centrifugal fan shall operate during each burner firing sequence and to pre-purge and post-purge the combustion chamber.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 20 Section “Motors.”

Minimum Motor Sizes:   [___Horsepower.]

RPM:  [1750] or [3450].

Electrical Characteristics:  [120 V, single phase] [480 V, three phase], 60 Hz.

Full-Load Amperes:  [___amperes.]

Minimum Circuit Ampacity:  [___amperes.]

Maximum Overcurrent Protection:  [___amperes.]

Gas Train:  Provide an approved manual shutoff gas valve and pressure regulator.  Include a 100 percent safety pilot with electronic flame supervision.  Gas Regulator shall have pressure gauge before and after gas regulator with pet-cock for isolating the gauge for repairs/calibrating.

Ignition:  Pilot shall be the spark ignition type with separate manual shutoff valve.  Pilot shall have electronic flame supervision.

Casing:

Jacket:  Sheet metal with snap-in or interlocking closures.

Control Compartment Enclosures:  NEMA 250, Type 1A.

Finish:  Baked-enamel protective finish.

Insulation:  Minimum 2-inch thick fiberglass insulation surrounding the boiler.

Combustion-Air Connections:  Inlet and vent duct collars.

Mounting base to secure boiler to concrete base.

boiler trim

All included devices shall be sized in accordance with ANSI B31.9, “Building Services Piping.”

Pressure Controllers:  Operating, firing rate, and high limit.

Safety Relief Valve:

Size and Capacity:  Relief valve shall be as required for equipment in accordance with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

Pressure Setting:  [___psig.]

Bronze Safety Valves:  Class 250, forged copper-alloy disc; fully enclosed steel spring with adjustable pressure range and positive shutoff; factory set and sealed.

Drip-Pan Elbow:  Cast iron with threaded inlet and outlet and threads in accordance with ASME B1.20.1.

Steam pressure gauge shall be a compound gauge, vacuum range shall be from 0 to 30 inches hg, pressure range minimum of 1-1/2 (one and one-half) the maximum operating pressure of the boiler, if the condensing boiler is generating steam.  The gauge shall have a siphon with pet-cock to isolate gauge for repairs/calibrating.

Water Column:  Provide minimum 12-inch (300-mm) glass gauge (sight-glass); shall be of the Tri-cock type.

Drain Valves:  Drain valves shall be a minimum NPS 3/4 (DN 20) or nozzle size with hose-end connection.

Blowdown Valves:  Provide factory-installed bottom and surface, slow-acting blowdown valves same size as boiler nozzle.

Blowdown Separator and Cooler:  Provide a blowdown separator manufactured in accordance with the requirements of Section VIII of the ASME Code and stamped by the National Board of Pressure Vessel Inspectors.  The separator shall be supported on a structural steel stand for mounting to foundation, include an after cooler with a [ manual ] [ automatic ] cooling valve assembly.(Note to Engineer: Select either manual cooling valve assembly or automatic cooling valve assembly.)

Stop Valves:  Boiler inlets and outlets, except safety relief valves or pre-heater inlet and outlet, shall be equipped with stop valve in an accessible location as near as practical to boiler nozzle and the same size as or larger than the nozzle.  Valves larger than NPS 2-inch shall have rising stem.

Stop-Check Valves:  Provide factory-installed stop-check valve at boiler outlet with free-blow drain valve factory installed between the two valves and visible when operating stop-check valve. The stop-check valve shall be sized in accordance with the boilers scheduled capacity.

Sample coolers:  Provide sample coolers for cooling hot steam vapor and hot blowdown samples from the boiler.

Burner operating controls

In order to maintain safe operating conditions, provide, as a minimum, the following burner safety controls to limit the operation of burner.

High Cutoff:  Automatic reset stops burner if operating conditions rise above maximum boiler design pressure of [___psig.].

Low-Water Cutoff Switch:  Float and electronic probe shall prevent burner operation on low water.  Cutoff switch shall be automatic-reset type.

Blocked Inlet Safety Switch:  Manual-reset pressure switch field mounted on boiler combustion-air inlet.

Alarm Bell:  Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Electric motors used for blowers

All electric motors used for blowers on burners and boiler trim pumps shall comply with the requirements of Section 11:  Energy Cost Budget Method and Table 10.2 of ASHRAE/IESNA Standard 90.1.

Boiler operating controls

Control systems for new boilers installed into existing conditions shall interface with existing control systems while having the characteristics specified herein.  Boilers installed in new conditions shall interface with the controls specified in this Section and Division 25, Building Automation Systems (BAS).

Boiler operating controls shall be microprocessor-based and shall include the following devices and features:

Control Transformer:  115 V shall be fed from a single dedicated electric circuit.  Controls and other ancillaries shall be sub-fed from the boiler control panel.

Operating Pressure Control:  Factory wired and mounted to cycle burner.

Low-Water Cutoff and Pump Control:  Cycle feedwater pump(s) for makeup water control.

Sequence of Operation:  Electric, factory-fabricated, and field-installed panel to control burner firing rate to maintain a constant steam pressure.  Maintain pressure set point plus or minus 10 percent.

Include automatic, alternating-firing sequence for multiple boilers.

Provide continuous digital read-out of the percent load of maximum heat input capacity during the boiler’s operation.

Building automation system interface

The boiler manufacturer shall provide factory-installed DDC microprocessor based hardware and software to enable the building automation system (BAS) to monitor and control the boiler and to display the boiler status and alarms specified in the Contract Documents.  Boiler controls shall interface seamlessly with other DDC microprocessor-based building subsystems as shown in the Contract Documents.  Interface shall be BACnet compatible.

The interface between the boiler controls and the BAS shall enable the BAS to read as separate and discreet points significant values and alarms on the boiler.  Use of a single set of contacts to send an alarm will not be acceptable.  Furnish and install the necessary hardware, wiring, computing equipment and software, as defined in the Contract Documents and as required, for the boiler to operate in accordance with the sequence of operation.

As a minimum the interface shall allow the following inputs, outputs and functions.

Boiler operating and alarm status.

Burner status.

Burner capacity.

Burner firing rate indication.

Boiler steam pressure.

Boiler tripped by high/low pressure or high/low temperature loss of electrical power.

Boiler steam flow.

High and low water level.

High and low gas/oil pressure.

Boiler supply / return water temperatures.

Boiler supply set point command (applicable only when not in conflict with design operation. All other instances shall be read only for boiler supply set point).

Fault annunciation with detail fault menus.

Fault history.

Connection to burner fan VFD.  Real time burner output and status indication.

O2 trim.

Real time O2/CO2 readout.

Real time readout of boiler efficiency.

Boiler feedwater control.

Stack temperature.

Each boiler shall be equipped with a totalizing non-reset fuel flow meter to monitor the usage of each fuel type.  Fuel flow meter shall have pressure and temperature compensation and have outputs that can be integrated into the BAS for real time fuel usage measurement and total fuel consumption. Interface shall be an analog signal for current usage and pulsed digital output for total usage directly wired to the BAS.

Venting kits and Flue VentING

General: The boiler flue venting system shall be provided in accordance boiler manufacturer’s recommendations for boiler compliance with Lo NOx emission standards for the St. Louis Area.  It shall be the responsibility of the boiler manufacturer to review the flue venting system and the boiler’s burner performance for Lo NOx compliance.  Refer to Specifications Section 23 51 00 – Breeching, Chimneys and Stacks for additional flue venting requirements.

Kit:  ASTM A 959, Type 29-4C, stainless-steel, [horizontal] [vertical] vent terminal, [wall] [roof] passage thimble, indoor wall plate, vent adapter, condensate trap, and sealant.

Combustion-Air Intake:  Stainless steel, [horizontal] [vertical] vent terminal with screen, inlet air coupling, and sealant.

Chimney and Type B Vent Adapter:  Vent adapter and sealant.

EXECUTION

PREPARATION

Before the boiler is installed, examine rough-in conditions for concrete equipment bases, anchor-bolt sizes and locations, and venting, piping and electrical connections to verify actual locations, sizes, and other conditions affecting boiler performance, maintenance, and operations.

Boiler locations indicated on the Drawings are approximate.  Determine exact locations before roughing-in for venting, piping and electrical connections.

Examine mechanical spaces to verify suitable conditions exist where the boilers will be installed.  Proceed with boiler installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Install boilers level on a concrete base.

Concrete Bases:  Boilers shall be anchored to concrete base.  For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into the structural concrete floor. Accurately place and secure anchorage devices.

Use setting Drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

Install anchor bolts to elevations required for proper attachment to supported equipment. Cast-in-place concrete materials and placement requirements shall be as specified in Division 03.

Install gas-fired boilers according to NFPA 54.

Install oil-fired boilers according to NFPA 31.

Assemble and install boiler trim.

Install electrical devices furnished with boiler but not specified to be factory mounted.

According to the "general waste water regulations" only waste water/sewage with a pH-value between 6.5 and 8.5 can be introduced into the sewage system.  With gas based condensing boiler systems the pH-value is between approximately 3.8 and 5.4. This range means that the condensate of the condensing process is an acid and so condensate from the combustion process cannot be introduced into the sewage system without further treatment/processing.  In regard to its introduction also its composition and its quantity are important depending on the origin of the natural gas, its composition can differ. The following applies for natural gas E (former natural gas H):

100% Natural gas-E = 93% CH4 + 4.9% CnHm + 1.1% N2 + 1% CO2

Connections:

Piping installation requirements shall be as specified in other applicable Division 23 Sections.  The Drawings indicate the general arrangement of piping, fittings, and specialties.

Connect piping full size to burner inlet with shutoff valve and a flanged or union type connection.

Connect steam and condensate piping to the supply and return and blowdown-boiler tappings with shutoff valve and union or flange and joint at each connection.

Install piping from safety valves to drip-pan elbow with the discharge of the valve through the roof and the drain piping to the nearest floor drain.

Connect flue vent to boiler outlet. Refer to Division 23 Section “Chimneys, Breechings and Stacks” for venting materials and flue venting sizing requirements.

Install piping adjacent to boiler to allow service and maintenance.

Ground equipment according to Division 26.

Connect wiring according to Division 26.

Tighten electrical connectors and terminals according to manufacturer’s published torque-tightening values.  If manufacturer’s torque values are not indicated, use torque values specified in UL 486A and UL 486B.

inspection

Inspection Process Overview:

Contractor shall complete and submit required forms to EOR including the boiler installation report and manufacturer’s data report thirty (30) days prior to the estimated boiler start-up date and notify the Owner’s Project Manager.

Owner’s Project Manager will notify Owner’s Authorized Inspector, Factory Mutual, that the inspection process has been initiated.

Contractor shall notify Owner’s Project Manager of the date that the boiler(s) will be opened for internal inspection upon EOR approval of the reports.

The Owner will coordinate with Owner’s Authorized Inspector, Factory Mutual, on the State boiler inspection.

A temporary certificate will be issued to the Owner for boiler Start-up.

The final certificate will be issued to the Owner.  Contractor shall mount final certificate at boiler location.

testing

Engage a factory-authorized service representative to test, inspect, and adjust the boiler and components, and to perform Start-up services.

Perform installation and Start-up checks according to manufacturer’s written instructions.

Leak Test:  Hydrostatic test.  Repair leaks and retest until no leaks exist.

Operational Test:  Start units to confirm proper motor rotation and unit operation.  Adjust air-fuel ratio and combustion controls.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Set field-adjustable switches and circuit-breaker trip ranges as indicated.

Occupancy Adjustments:  When requested by Owner within 12 months of Substantial Completion date, provide on-Site assistance in adjusting system to suit actual occupied conditions.  Provide up to two (2) visits to the Project Site outside normal occupancy hours for this purpose, without additional cost to the Owner.

Prepare a written report that documents testing procedures and results.

END OF SECTION 23 52 39