SECTION 23 57 10 – Unfired Steam Generators

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide and install unfired steam generators with the required trim components and all related appurtenances to make a complete, functioning and operational system that will supply clean steam for humidification and sterilizer equipment.

Steam Generators, Steam to Steam using Potable Soft Water.

Steam Generators, Steam-to-Steam using Reverse Osmosis (RO) or Deionized (DI) Water.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within all references.

QUALITY ASSURANCE

Conform to ANSI/ASME Boilers and Pressure Vessels Code Section VIII, Division 1 for design and fabrication of pressure vessels for manufacture of tubular heat exchangers and heat exchanger shells.

Factory testing of the steam heat exchanger units shall be in strict conformance with all applicable sections of the ASME code and shall bear the standard ASME symbol.

All equipment or components of this Section shall meet or exceed the requirements and quality of items specified and as indicated on the Drawings.

Ensure that equipment pressure ratings are at least equal to system’s maximum operating pressure at point where installed, but not less than specified.

Equipment manufacturer shall be a company specializing in manufacture, assembly, and field performance of provided equipment with a minimum of five (5) years experience.

Ensure pump operation at specified system fluid temperatures without vapor binding and cavitation, is non-overloading when the pump is operating in parallel or individual operation.

Where applicable, the manufacturer shall be listed by Underwriter's Laboratories as a manufacturer of packaged pumping systems.

SUBMITTALS

Product Data:

Submit product data including certified rated capacities, performance curves of selected model, weights (shipping, installed, and operating), furnished specialties, and accessories.  Indicate the feedwater pump’s operating point on volume flow and head pressure curves.

Record Documents:

Submit Shop Drawings and product data, including footprint dimensions, pipe sizes, pipe descriptions, pipe arrangement, and electrical and control panel Drawings.

Submit dimensioned floor plan Drawings with all related system piping, equipment piping and support locations.

Submit manufacturer’s installation instructions.

Submit pressure test reports of vessel shell and tube bundle pressure tests.

Operation and Maintenance Data:

At project closeout, submit operation and maintenance data that includes start-up and shut down instructions, assembly Drawings, a spare and replacement parts lists.

DELIVERY, STORAGE and HANDLING

Deliver, store, protect and handle products to the Project Site under provisions of Division 01 and Division 20.

Protect internals from entry of foreign material by temporary caps on flanged openings.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

manufacturers

Acme Engineering Products, Inc.

Patterson-Kelley, Company.

Ace Boiler, Inc.

Cemline, Corporation.

Precision Boilers, Inc.

Unfired Steam Generators – Steam to Steam

Unfired steam generators shall be furnished as a complete package ready for installation including all necessary components for operation.  The unfired steam generator, steam to steam type, shall be of the sizes and capacities noted on the Drawings. The generator shall consist of specified materials and components and shall be specifically designed for working pressure scheduled.   The unfired steam generator selection shall be provided with the scheduled minimum heat transfer surface area required to meet the scheduled capacity and pressure drops.  The unfired steam generator shall be factory mounted, wired, piped, and tested.

Unfired steam generators shall be ASME Code constructed and stamped in accordance with Section VIII, Division I, for Unfired Steam Generators and shall be U.L. listed.  Generators shall be registered with the National Board of Boiler and Pressure Vessel Inspectors, and a signed copy of the shop inspection report shall be furnished to the Owner.  When generating steam above 50 psi, generator welds shall be 100 percent x-rayed in accordance with Section VIII “Unfired Steam Generators” and shall bear the “UB” stamp.  When generating steam below 50 psi, generators shall be in accordance with Section VIII “Unfired Steam Generators” and shall bear the “UB” stamp.

Mount on a suitable I-Beam support skid, which shall be permanently welded to the shell.

Insulate with not less than 2 inches of fiberglass insulation, protected by not less than 20 gage thick-enameled steel jacket.

Furnish with materials appropriate for the generated steam fluids noted on the Drawings.

Generated Steam Fluid– Potable Water (Soft water of less than 8 grains of hardness):

Construct of a carbon steel shell with NPT or flanged carbon steel supply connection.

Furnish with submerged u-tube type heat exchanger coil.  On generators where the source steam pressure exceeds 80 psig, 18 gage 90/10 cupro-nickel tubes shall be provided on the coil.  Where the source steam pressure is less than 80 psig, 20 gage copper tubes shall be provided on the coil.  Tubes shall be expanded into a tubesheet of the appropriate tubesheet material for the tubing being used.  Tubes shall be arranged in the tubesheet in a two-pass arrangement with a triangular pitch.

All components subject to the generated steam side shall be of copper or carbon steel construction.  Component piping on generated steam side shall be carbon steel or copper.

Furnish with a vessel steam gauge and pressuretrol to monitor the generated steam.  Gauge shall be of copper or brass construction with a steel case and shall be of the appropriate range for the generated steam pressure.

Furnish with a carbon steel float type level controller with a steel water column and gauge glass assembly.

Furnish with an ASME Code Section I brass pressure relief valve with a capacity to relief the total BTU output of the generator.

Furnish with a vacuum breaker.

Blowdown components shall be of copper or carbon steel construction.  Blowdown piping on generated steam side shall be carbon steel or copper.

Unfired steam generators operating at 15 psi or below shall be furnished with a brass feed water solenoid valve (factory wired to level control), carbon steel check valve, and high limit solenoid valve.  Unfired steam generators operating above 15 psi shall be additionally furnished with a multistage feed water pump sized to generate adequate feedwater pressure for the scheduled generated steam pressure and capacity.  Pump shall be factory supplied with a starter wired to the level control.  The pump shall discharge into a brass ball valve, brass feed water solenoid valve (factory wired to level control), carbon steel check valve, and high limit solenoid valve.

On systems where source fluid water hardness is higher than 10 grains of hardness a water softener shall be provided to soften water to less than 8 grains of hardness to minimize scaling on the unit.

Generated Steam Fluid– DI or RO Water:

Construct of Type 316L stainless steel shell with NPT or flanged stainless steel supply connection.

Furnish with submerged u-tube type heat exchanger coil.  On generators where the source steam pressure exceeds 80 psig, 18 gage Type 316L stainless steel tubes shall be provided on the coil.  Where the source steam pressure is less than 80 psig, 20 gage stainless steel shall be provided on the coil.  Tubes shall be expanded into a Type 316L stainless steel tubesheet.  Tubes shall be arranged in the tubesheet in a two-pass arrangement with a triangular pitch.

Components subject to the generated steam side shall be Type 316L stainless steel construction.  Component piping on generated steam side shall be stainless steel.

Furnish with a vessel steam gauge and pressure transmitter to monitor the generated steam.  Gauge shall be of stainless steel construction with a stainless steel case and shall be of the appropriate range for the generated steam pressure.

Furnish with a stainless steel float type level controller with Type 316L stainless steel water column.

Furnish with an ASME Code Section I stainless steel pressure relief valve with a capacity to relief the total BTU output of the generator.

Furnish with a vacuum breaker.

Blowdown components shall be of stainless steel construction.  Blowdown piping on generated steam side shall be stainless steel up to the condensate cooler.

Unfired steam generators operating at 15 psi or below shall be furnished with a stainless steel feed water solenoid valve (factory wired to level control), stainless steel check valve, and high limit solenoid valve.  Unfired steam generators operating above 15 psi shall be additionally furnished with a multistage feed water pump (with stainless steel wetted components) sized to generate adequate feedwater pressure for the scheduled generated steam pressure and capacity.  Pump shall be factory supplied with a starter wired to the level control.  The pump shall discharge into a stainless steel ball valve, stainless steel feed water solenoid valve (factory wired to level control), stainless steel check valve, and high limit solenoid valve.

All unfired steam generator components subject to the source steam side shall be of copper or carbon steel construction.  Component piping on source steam side shall be carbon steel or copper.

Furnish with a source steam gauge to monitor the source steam pressure.  Gauge shall be of copper or brass construction with a steel case and shall be of the appropriate range for the source steam pressure.

Furnish with a pilot actuated control valve to modulate incoming steam to maintain desired output of steam pressure +/- 2 psi.  Control valve shall be suitable for 150 psi at 300 degrees F.  Control valve pilot pressure transmitter shall monitor output steam pressure and modulate the boiler steam to maintain constant output pressure.

Factory supply with dual float and thermostatic traps, one for the coil and one for the drip before the control valve.  Provide an incoming steam strainer.

Furnished with an internal steam separator.

Factory furnish with a high water shut-off.  High water shut-off shall include an electronic probe mounted in the top of the unit connected to an electric operated power to open spring to close ball valve for boiler operating at or below 15 psi.  For boilers operating above 15 psi steam, high water shut-off shall open the feed water pump circuit. In the event of high water, the ball valve will close.

Provide with dry contacts to alert the building automation system (BAS) of either a high pressure, low water, or high water condition occurs.  Additionally, the unit shall be provided with a 120-volt alarm bell that is factory wired to sound at any of these conditions.  Furnish with an alarm-silencing relay with red alarm light and manual push button.

Furnish with a relay for remote on-off control from the BAS system.

Furnish with a TDS Blow Down system.  A factory installed time sample feed water blow down system consisting of a control, which measures the total dissolved solids in the generator.  The blow down operates on a timed basis and if the total dissolved solids exceed the set point, the valve shall blow down the boiler until fresh water brings the total dissolved solids level to the desired setting.  Automatic blow off system shall be furnished with a NEMA I control system and be factory wired to a single point 120 volt connection.  Field piping of cold water to the unit’s mixing valve and venting from the unit shall be the responsibility of the Contractor.

Factory furnish with a factory-mounted blow down \ condensate cooler, ASME code constructed, and stamped for 150 psi working pressure.

Minimum steel thickness is 3/16 inches.  The blow down enters the tangential inlet where it meets a 90 degree stainless steel wear plate.  The wear plate will prevent erosion of the sidewall of the vessel.  The tangential blow down entry causes the blow down to swirl around the circumference of the vessel where part of the liquid will flash to steam and the balance will settle to the bottom.  The internal flash will go through the vent to atmosphere and the hot condensate and sludge will fall to the bottom of the vessel where it will flow by gravity to the drain leg.  The temperature of the condensate will activate the thermal control valve, which will feed cold water into the drain leg where the cold water and hot condensate will mix.  This results in drained liquid temperature less than 140 degrees F which is acceptable for municipal sewage.  A thermometer is furnished in the drain leg and a check valve is furnished on the coldwater inlet.  Tank shall be mounted and piped as part of the Unfired Steam Generator package.

Furnish as factory packages with all wiring to single terminal strip and factory pipe for field connections to city water, source steam, source steam condensate, clean steam outlet, drain, and relief valve outlets.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Install to permit removal of steam tube bundle with minimum disturbance to installed equipment and piping.

Pitch shell to completely drain condensate.

Pipe drain valves to nearest floor drain.

Install dielectric fittings where ferrous metal and non-ferrous metal are in contact.

Proper access space around a device should be planned for servicing the component.  Provide no less than the minimum recommended by the manufacturer.

Provide an adequate number of isolation valves for service and maintenance of the system and its components.

Provide temperature and pressure gauges where shown on Drawings and as directed by Owner.

All piping shall be brought to equipment and pump connections in such a manner so as to prevent the possibility of any loads or stresses being applied to the connections or piping. All piping shall be fitted to the pumps even though piping adjustments may be required after the pipe is installed.

On condensate coolers that require cooling water for condensate temperature reduction, provide cooling water supply piping and connections as required.  Piping should be of adequate size to pass required flow rate.

On components that require draining, route piping to appropriate drains for discharge.

On components that require venting, provide vent piping from equipment vent connections and pipe to appropriate discharge location.

testing

Proper component start-up practices and procedures shall be followed on all components.  Provide no less than the minimum as recommended by the manufacturer.

Equipment provider shall be responsible for providing certified equipment Start-up.

New equipment Start-up shall be for the purpose of determining equipment operation, voltage, and amperage readings.

Confirm all proper electrical connections, pump’s balance, discharge and suction gauge readings, and adjustment of head, if required.

Provide Start-up reports outlining factory provided Start-up and equipment performance.

training

Manufacturer's representative shall instruct Owner’s personnel in the care of the equipment by conducting training session(s).

END OF SECTION 23 57 10