SECTION 23 82 33 – electric duct heaters

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide and install the following electric duct heaters indicated by the Contract Documents with supplementary items necessary for proper installation.

Refer to Division 26 sections for the following Work:

Power supply wiring from power source to power connection on terminal unit.  Include starters, disconnects, and required electrical devices, except where specified as furnished, or factory-installed, by manufacturer.

Interlock wiring between electrically-operated terminal units and between terminal units and field-installed control devices.

Interlock wiring specified as factory-installed is Work of this Section.

Provide the following as Work of this Section, complying with requirements of Division 26 Sections:

Control wiring between field-installed controls, indicating devices, and terminal unit control panels.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

ARI Standard 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.

ASHRAE Standard 33 - Methods of Testing Forced Circulation Air Cooling and Heating Coils.

National Fire Protection Association (NFPA) 70, National Electrical Code.

ANSI/UL 883 - Safety Standards for Fan Coil Units and Room Fan Heater Units.

ANSI/UL 1025 - Electric Air Heaters.

ANSI/ NFPA 70 - National Electrical Code for components and installation.

ANSI/UL 1096 - Electric Central Air Heating Equipment.

QUALITY ASSURANCE

Manufacturer's Qualifications:  Firms regularly engaged in manufacture of electric duct heaters, of types and sizes required, whose products have been in satisfactory use in similar service for not less than three (3) years.

Codes and Standards:

Provide coil ratings in accordance with American Refrigeration Institute (ARI) Standard 410 "Forced-Circulation Air-Cooling and Air-Heating Coils".

Test coils in accordance with American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE) Standard 33 "Methods of Testing Forced Circulation Air Cooling and Heating Coils".

Provide electrical components for terminal units, which have been listed and labeled by UL.

SUBMITTALS

Product Data:

Submit manufacturer's data for duct heaters showing dimensions, capacities, ratings, performance characteristics, gages and finishes of materials, and installation instructions.

Record Documents:

Manufacturers wiring diagrams detailing electrical connection to duct heaters for wiring for power, signal, and control systems, differentiating clearly between manufacturer-installed wiring and field-installed wiring.

DELIVERY, STORAGE and HANDLING

Deliver, store, protect and handle products to the Project Site under provisions of Division 01 and Division 20.

Accept products at the Project Site in factory-fabricated protective containers or coverings, with factory-installed shipping skids.  Inspect for damage.

Store in clean dry place and protect from weather and construction traffic.  Handle carefully to avoid damage to components, enclosures, and finish.

Check and maintain equipment on a monthly basis to ensure that equipment is being stored in accordance with manufacturer’s recommended practices. Storage records shall be maintained that indicate these requirements have been met.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Electric duct heaters of types, sizes, ratings, and characteristics indicated.

Heating Elements:  Open coil of resistance wire, 80 percent nickel and 20 percent chromium, supported and insulted by floating ceramic bushings.  Recess bushings into casing opening and fasten to supporting brackets.  Mounted in galvanized-steel frame.

Coil Layout:  Horizontal (air flow vertical) or Vertical (air flow horizontal).

Casing Assembly:  Slip-in type, galvanized-steel frame.

Over-Temperature Protection:

Serviceable through terminal unit without removing heater from duct or unit.

Disk-type, automatic reset, thermal-cutout safety devices for primary over-temperature protection.

Load carrying, manual reset or manually replaceable thermal cutouts, factory wired in series with each heater stage for secondary protection.

Airflow switch, diaphragm operated differential pressure switch to prevent duct heater from operating when there is no air flow.

Control Panel:  Mounted on unit, with means of a safety disconnect and overcurrent protection.   Include the following controls:

Magnetic contactor.

Silicon-Controlled Rectifier (SCR)] or Step controller with integrated Vernier Stage using 4 to 20 ma or 1 to 10 Volt input signal.

Time-delay relay.

Pilot lights; one per step, “power on”, and “low air flow”.

Provide common ohmic voltage and milli-amp alarm signals to the building automation system (BAS).

Provide single point power connection.

Permanently attach a separate, complete, and specific wiring diagram to each heater.  Typical wiring diagrams are not acceptable.  Clearly mark power and control terminals in terminal unit identical to the wiring diagram.

manufacturers

Chromalox.

Indeeco.

Markel Products Co.

Nailor Industries, Inc.

Trane Inc.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Inspect areas and conditions under which terminal units are to be installed.  Do not proceed with Work until unsatisfactory conditions have been corrected in manner acceptable to installer.

Do not operate electric heaters for any purpose until ductwork is clean of any possible debris.

Maintain minimum working clearances around the heater electrical panel in accordance with NEC Article 110.

Install duct heaters in metal ducts and casings constructed according to SMACNA “HVAC Duct Construction Standards.”

If applicable, anchor duct heaters in position using suitable supports.

Connect duct heaters and components to wiring systems and to ground as indicated and instructed by manufacturer.  Tighten connectors and terminals’, including screws and bolts, according to equipment manufacturer’s published torque-tightening values for equipment connectors.  Where manufacturer’s torque requirements are not indicated, tighten connectors and terminals according to tightening torques specified in UL 486A.

After construction is completed, including painting, clean unit’s exposed surfaces and vacuum clean electric duct heaters and inside of cabinets.

Touch up scratches and marks from handling and placement of equipment with masking enamel to match manufacturer's color.  Refer to Division 09 for Site-applied finishes.

END OF SECTION 23 82 33