SECTION 26 08 13 – electrical systems prefunctional checklists and start-ups

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

This Section expands on and defines responsibilities of the Contractor regarding Prefunctional Checklists and start-up portions of the Commissioning process and addresses validation of proper and thorough installation of mechanical, plumbing and fire protection systems.

Contractor shall oversee the Commissioning activities with the Contractor’s Subcontractors and the Architect/Engineer (AE).

Contractor shall completely install, thoroughly inspect, start-up, test, adjust and integrate Electrical Testing Agency (ETA) on systems and equipment.  All activities shall be documented on specific, procedural forms developed for that purpose.  Contractor shall notify AE and Owner in writing that systems are complete and ready for verification and Functional Performance Tests.

Completed Prefunctional Checklists for all pieces of equipment shall be submitted to the Owner prior to Functional Performance testing.

Responsibilities of the various parties involved in the Commissioning process are defined in Section 26 08 00.

Refer to Attachments A, B, C, and D at the end of this Section for example forms that indicate level of documentation required for the Commissioning process.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with all applicable requirements and standards.

SUBMITTALS

Prefunctional Checklists, Prefunctional Tests, and Start-up documents are the normal procedure of ensuring that the mechanical, plumbing, and fire protection system components are properly installed.

The Subcontractor in cooperation with the AE and Contractor shall develop Prefunctional Checklists and Prefunctional Tests during the Construction Phase.

Completeness of Prefunctional Checklists:  This Section summarizes the minimum standard for systems and equipment checkout.  A record of testing and acknowledgement that a procedure has been completed and that it checks out acceptably must be included in the Prefunctional Checklists.  The Prefunctional Checklist shall identify in columnar format each device, location, test method, control sequence of operation reference, device code reported, and other data as appropriate.

Equipment Data Documentation:  Provide completed, as-installed, specific product nameplate data, product numbers, serial numbers, etc. to fully define the asset for Owner’s use in maintenance management and asset tracking.  This data may be incorporated within the Equipment List/Matrix as described in Division 01 as a spreadsheet format or electronic database. In addition to specific manufacturer’s name and specific product identifiers such as model number, serial numbers, date of manufacture, etc, the following information shall be included with the equipment data documentation:

Capacity data:  Where applicable, use equipment schedules on the Drawings as a guideline for fields to be used.

Location identifier field for each of the three dimensions (Floor Level, X axis, and Y axis) using the Drawing column grids as the basis for location.

Submit the equipment data documentation with the draft Prefunctional Checklists to the Owner for approval.  AE and Owner will review the Prefunctional Checklists and request any additional information required to meet the Commissioning Plan criteria.

Written Certification:  The Contractor shall certify that the installation, Start-up, Prefunctional Checklist, and initial operation of the system or component is in accordance with the Contract Documents, Commissioning Plan, and manufacturer’s requirements, and that the system is ready for Functional Performance Tests.  Any outstanding items or non-conformance shall be clearly indicated and highlighted on the Prefunctional Checklist and an action item shall have been initiated.  Refer to Division 01 for specific details on non-conformance issues relating to Prefunctional Checklists.

Refer to Section 26 08 00 for additional documentation requirements.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

The Prefunctional Checklist procedures described in this Section provide minimum guidelines for development of Prefunctional Checklists; Start-up procedures, and Prefunctional Tests.  Contractor shall prepare the Prefunctional Checklists using these procedures and that of the manufacturer’s and/or applicable codes and standards.

The Prefunctional Checklist form shall acknowledge that installation and Start-up procedures were successfully adhered to and completely performed and shall document relevant parameters (panel and equipment connections, measured values, ground faults, trip settings, etc.).  When indicated as performing a checkout on multiple items or multiple procedure items, Prefunctional Checklist forms shall itemize each individual item.

TEST EQUIPMENT

Refer to Section 26 08 00 – Electrical Systems Commissioning.

EXECUTION

PREFUNCTIONAL CHECKLIST PROCEDURES

[Edit the following as appropriate for the Project:]

Thermographic Scanning:

Contractor shall provide thermographic scanning on all switchgear and distribution boards.  In general, the thermographic scanning shall be made when the equipment is energized and is operating at its normal capacity.  It is intended that the scan be made after the equipment has been in full operation; however, the Contractor near the completion of the Project will determine the exact time of conducting the scan.  Some scanning for occupant-created load shall be performed during the Warranty Period as a Deferred Test.

Test equipment, miscellaneous tools, and materials shall be transported properly, moved, and set up by trained personnel.  Equipment used in testing shall be capable of performing all recommended procedures required by the apparatus and related equipment.  All test equipment shall have certification of calibration and be in working order.

All hot spots shall be marked, identified, and an infrared thermographic scanning report prepared and furnished to the Owner.

The report shall contain infrared photos of trouble spots with temperature readings.

The Contractor shall promptly report all sources of heating problems to the Owner for corrective action.

Grounding Systems:

Perform three-point fall-of-potential test per Institute of Electrical and Electronics Engineers (IEEE) Standard 81 on the main grounding electrode or system.  Resistance shall be no greater than 5 ohms.

Perform the two-point method test per IEEE Standard 81 to determine the ground resistance between the main ground system and all major electrical equipment frames, system neutral, and/or derived neutral points.  Resistance shall be no greater than 5 ohms.

AC Motors – General Across Systems:

Verify proper alignment, installation, and rotation.

Measure the insulation resistance, phase balance, and resistance to ground.  This measurement will generally be the responsibility of the electrical Subcontractor who is connecting the motor.  Correction of any deficiencies will be the responsibility of the motor supplier.  Where the electrical Subcontractor wires to a single point of a packaged device that is shipped with multiple motors, electrical Subcontractor shall check all motors in the package.

Verify that properly sized overloads are in place.

Measure voltage available to all phases at time of initial connection and again after motor has been placed in operation under load measure amps and RPM.

Record all motor nameplate data.

High Voltage Primary Service Feeders:

Start-up checklists:  Perform the following final checks before Start-up:

Inspect underground duct banks.

Inspect cable and perform field testing on reels.

Inspect splicing and terminations.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  Exposed cable, compression type terminations, splices where approved by the Engineer and the Owner, and fire proofing in manholes, cable vaults, etc.

Correct color code identification and phasing arrangements.

Perform shield continuity test.

Perform insulation resistance test on new and existing cables.

Perform high potential test on new cables only.

High Voltage Primary Disconnect and Grounding Switches:

General:  Provide the services of a factory-trained manufacturer’s representative to assist the Contractor in the installation and start-up service of the equipment and to train Owner's personnel as specified.

Start-up checklists:  Perform the following final checks before Start-up:

Inspect incoming power cable terminations.

Inspect transformer connections.

Inspect grounding.

Inspect electrical interlock wiring.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  anchoring, grounding, oil level, torque of bus and cable connections, and mechanical operation of switch and operating mechanisms.

Perform contact resistance test.

Conduct and review oil sample tests.

Perform insulation resistance tests on switch and control wiring.

Perform electrical and mechanical (key) interlock system operations.

High Voltage Transformer:

Provide the services of a factory-trained manufacturer’s representative to assist the Contractor in the installation and start-up service of the equipment and to train Owner's personnel as specified.

Start-up checklists:  Perform the following final checks before Start-up:

Inspect primary and secondary power connections.

Inspect control interconnections.

Inspect grounding.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  vibration isolation, anchoring, grounding, installation verification using manufacturer’s checklist, flexible bus connections, torque of bus and cable connections, and tap changer operation.

Verify operation of temperature controls/alarms.

Perform winding insulation tests.

Conduct turns ratio test.

Perform power factor/dissipation test on windings and bushings.

Perform high voltage and low voltage winding and core resistance measurements.

Check and confirm percentage of impedance is identical for all three transformers comparing nameplates.

600V Network Protectors/480V Secondary Distribution:

Provide the services of a factory-trained manufacturer’s representative to assist the Contractor in the installation and start-up service of the equipment and to train Owner's personnel as specified.

Start-up checklists:  Perform the following final checks before Start-up:

Inspect transformer connections.

Inspect 600V disconnect connections.

Inspect grounding.

Validate protector element installation (furnished loose).

Verify control interconnections.

Check calibration/setting of protective devices from system coordination study.

Verify calibration/setting of digital metering.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  anchoring, grounding, torque of bus/cable connections, operational check of drawout mechanism, manual/electrical trip/close operations, contact closure using slow closing method, arc chute inspection, and installation verification using manufacturer's checklist.

Correct current transformer ratios.

Conduct contact resistance test.

Perform operational/functional tests of protective relaying.

Perform operational/functional tests of digital metering.

Perform electrical and mechanical (key) interlock system operational tests.

Conduct operational voltage testing with line voltage from transformer only and/or source feeder breaker open.

600V Disconnect Switches/480V Secondary Distribution:

Provide the services of a factory-trained manufacturer’s representative to assist the Contractor in the installation and Start-up service of the equipment and to train Owner's personnel as specified.

Start-up checklists:  Perform the following final checks before Start-up:

Inspect protector and bus duct connections.

Inspect grounding.

Verify control interconnections.

Check installation of warning nameplates.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  anchoring, grounding, torque of bus/cable connections, and mechanical operation of switch and operating mechanisms.

Conduct insulation resistance tests on switch and control wiring.

Conduct contact resistance test.

600V Service Switchgear/480V Secondary Distribution:

Provide the services of a factory-trained manufacturer’s representative to assist the Contractor in the installation and Start-up service of the equipment for a period of three (3) working days in three (3) visits and to train Owner's personnel as specified.

Start-up checklists:  Perform the following final checks before Start-up:

Inspect connections to main breakers.

Inspect grounding.

Inspect feeder connections to busways and cables.

Inspect installation of main, tie and feeder breaker elements.

Inspect control and alarm interconnections.

Check calibration/setting of trip devices using system coordination study.

Verify calibration/setting of digital metering.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  anchoring, grounding, torque of feeder and incoming bus duct connections, feeder cable and integral main bus connections, switchgear section alignments, electrical clearances, mechanical operation of breaker/fuse drawout elements and operating mechanisms, manual trip function, main bus safety shutters, and installation verification using manufacturer's checklist.

Check current and potential instrument transformer ratios.

Conduct insulation resistance and over potential tests on each type of each breaker element contacts, switchgear control wiring, breaker element control wiring and each bus section.

Conduct resistance test through switchgear bus joints.

Conduct current test using primary or secondary current injection.

Conduct phasing test on triple-ended switchgear.

Conduct contact resistance test on each type breaker element.

Conduct ground resistance test.

Conduct operational/functional tests of protective relaying.  Time-current tests shall be conducted and trip points shall be set per Architect/Engineer’s direction.

Conduct operational/functional tests of digital metering.

Perform electrical and mechanical (key) interlock system operational tests on generator and service switchgear.

600V Feeder and Subfeeders/480V Secondary Distribution:

Start-up checklists:  Perform the following final checks before Start-up:

Inspect cable terminations.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  large junction and pull boxes, supports of raceways and cable bus, and compression type terminations.

Correct identification and phasing arrangements.

Conduct continuity test of each feeder.

Conduct insulation resistance test of each feeder.

600V Motor Control Centers / 480V Secondary Distribution (16400:

Start-up checklists:  Perform the following final checks before Start-up:

Inspect cable terminations.

Check installation and setting of overload relays.

Inspect control interconnections.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  anchoring, grounding, torque of feeder and incoming connections, electrical clearances, starter and feeder unit drawout mechanisms, and check installation using manufacturer's checklist.

Perform test of overload relays for each size starter using primary current injection methods.

Conduct operational tests of starters through local/remote controls.

Conduct insulation resistance test on MCC busing, each type motor starter unit (except for variable frequency drives), and each control circuit.

Conduct contact resistance and insulation resistance test of molded case main and feeder circuit breakers.

Distribution Transformers/480V Secondary Distribution:

Start-up checklists:  Perform the following final checks before Start-up:

Inspect wiring connections.

Insure taps are adjusted.

Inspect grounding.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following: mounting, grounding, electrical clearances, and K factor and/or isolating transformers are installed where required.

Perform insulation resistance, turns ratios, and polarity tests on each type /size of transformer.

Distribution and Branch Circuit Panelboards/480V Secondary Distribution:

Start-up checklists:  Perform the following final checks before Start-up:

Inspect wiring connections.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following: mounting, separate ground and neutral connections per circuit, completed circuit directories, electrical clearances, KAIC ratings of panelboard and breakers.

Correct surge suppression devices installed.

Review current readings for each panelboard to ensure loads are balanced.

Conduct insulation resistance tests.

600V Branch Circuits/480/208/120V Secondary Distribution:

Start-up checklists:  Perform the following final checks before Start-up:

Inspect wiring connections.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  large junction and pull boxes, supports of raceways, and compression type terminations.

Correct identification and phasing arrangements.

Perform random continuity test of any branch circuit.

Receptacle Polarity Test:  Test every receptacle installed or reconnected under this Contract with a receptacle circuit tester.  Tester shall test for open ground, reverse polarity, open hot, open neutral, hot and ground reversed, hot or neutral and hot open.  Rewire receptacles with faults and retest.

Ground-Fault Receptacle Circuit Interrupter Tests:

Test each receptacle or branch circuit breaker having ground-fault circuit protection to assure that the ground-fault circuit interrupter will not operate when subjected to a ground-fault current of less than 4 milliamperes and will operate when subjected to a ground-fault current exceeding 6 milliamperes.

Perform testing using an instrument specifically designed and manufactured for testing ground-fault circuit interrupters.  "TEST" button operation will not be acceptable as a substitute for this test.

Replace receptacles that do not shutoff power with 5/1000 of an ampere within 1/40th of a second and retest.  Submit test report signed by Test Engineer who performed this test.

Lighting Fixtures and Lighting Controls / 277 / 120V Lighting:

Provide the services of a factory-trained manufacturer’s representative to assist the Contractor in the installation and Start-up service of the lighting control system and train Owner's personnel as specified below.  Representative will confirm the proper installation and operation of all system components.

Start-up checklists:  Perform the following final checks before Start-up:

Ensure all labeling is affixed and accurate.

Verify quantity, type and location of fixtures.

Verify type and location of switches.

Ensure all terminations are tight.

Check sensor placement is adequate for required duty.

Ensure adequate access is provided to all panels and that documentation of that panel is provided in it.

Ensure all circuits for the loads are energized and ready for testing.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Test, calibrate, and set all digital and analog sensing, and actuating devices.

Calibrate each instrumentation device by making a comparison between the graphic display and the reading at the device, using an instrument traceable to the National Bureau of Standards, which shall be at least twice as accurate as the device to be calibrated (e.g., if field device is +/-0.5 percent accurate, test equipment shall be +/-0.25 percent accurate over same range).

Record the measured value and displayed value for each device in the Prefunctional Checklist.

Check each digital control point by making a comparison between the control command at the control panel and the status of the controlled device.

Check each digital input point by making a comparison of the state of the sensing device and the OI display.

Record the results for each device in the Building Automation System Start-up checklist.

Verify operation of lighting controls (dimming, photo-control, regular switching).

Check loads on all breakers to ensure that the breaker is properly sized.

Enter all schedules per occupant’s direction.

For Operator Interfaces: Verify all elements on the graphics are functional and properly bound to physical devices and/or virtual points and that hot links or page jumps are functional and logical.

Output all specified reports for review and approval.

Verify the alarm printing and logging is functional and per requirements.

Validate all interfaces with other systems on a point by point basis.

Lightning Protection System:

Start-up checklists:  Perform the following final checks before Start-up:

Inspect wiring connections.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Visually and mechanically inspect to include the following:  air terminal mountings, bonding connections of roof mounted HVAC equipment, down leads routing/roof penetrations, and grounding.

Review UL test certification.

Check for receipt of UL master label.

Fire Alarm Equipment / Fire Alarm and Detection System:

Provide the services of a qualified fire alarm specialist to supervise the installation, make adjustments, and perform tests on the fire alarm system and to train Owner's personnel.

Start-up checklists:  Perform the following final checks before Start-up.

Ensure all labeling is affixed and accurate.

Ensure all terminations are tight.

Ensure adequate access is provided to all panels and that documentation of that panel is provided in the panel.

Review that all fire alarm devices as shown on the construction Drawings and Shop Drawings are installed.

Review height and locations of pull stations and visual alarms to comply with ADA.

Review that smoke and duct detectors are installed according to NFPA 90A.

Check that fire alarm system control panel is clear with no trouble or ground faults.

Sprinkler flow and tamper switches have been adjusted.

Check wire supervision on all devices.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Check location of all sensors and switches to ensure conformance with requirements.

Cause activation of all device, assure alarms are initiated and resulting response is per the requirements.

Verify interfaces with all other inter-related systems or equipment including building automation system (BAS), sound systems, security systems, HVAC systems, vertical delivery systems, etc. on a point by point basis for all points

Validate all output devices (speakers and strobes) meet the code criteria (96 dBa at 10 feet and 117 candela at peak).

Activate high temperature detectors in the elevator machine room.  Verify all sequences including elevator shunt off, elevator recall including alternate floors when main floor is in alarm.

Activate all sprinkler flow switches.  Validate that appropriate zone enunciates and alarms sound.

Verify audio aspects of the system function as required.  Verify paging messages can be heard throughout the building.

For annunciator panels, validate correct graphic and correct identification of all zones.  Test the action and interlocks of all override switches as appropriate

For Operator Interfaces:

Verify all elements on the graphics are functional and properly bound to physical devices and/or virtual points and that hot links or page jumps are functional and logical.

Output all specified reports for review and approval.

Verify the alarm printing and logging is functional and per requirements.

Validate all interfaces with other systems on a point by point basis.

Grounding/Building Grounding System:

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Conduct fall of potential ground resistance tests per IEEE Standard 81 at each test well and at service equipment.

Conduct insulation resistance, short circuit, and ground tests of each motor.

Uninterruptible Power Systems (UPS):

Provide the services of a manufacturer certified specialist to supervise the installation, make adjustments, and perform tests on the UPS and to train Owner's personnel.

Automatic Transfer Switches:

Provide the services of a manufacturer certified specialist to supervise the installation, make adjustments, and perform tests on the automatic transfer switches and to train Owner's personnel.

Start-up checklists:  Perform the following final checks before Start-up:

Visually inspect the systems.

Ensure the terminations are tight and all ancillary equipment completely installed.

Ensure all overloads are in place.

Measure contact resistance.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Energize Switch.

Check positive interlock between systems.

Set/Calibrate Voltage sensing relay, transfer time delays (in both directions), and synchronization relays.

Measure insulation resistance and resistance to ground.

Check manual bypass operation.

Emergency Power Engine Generators and Distribution Systems:

Provide the services of a manufacturer certified specialist to supervise the installation, make adjustments, and perform tests on the engine generators and emergency power switchgear and to train Owner's personnel.

Start-up checklists:  Perform the following final checks before Start-up:

Visually inspect the systems.

Ensure the terminations are tight on power and control wiring.

Verify all ancillary equipment completely installed.

Ensure all overloads are in place.

Verify that generator is set in place.

Verify fuel connections.

Verify radiator connections.

Verify battery connection.

Verify exhaust connections.

Verify block or oil heater connection.

Check and record engine oil level, radiator water level, and battery electrolyte level.

Piping System Tests:  Complete system test in accordance with the respective section.

Inspect the installation and access/clearance for service and maintenance to ensure it meets the Project and manufacturer’s requirements.

Check lubricating oil for lubricated-type equipment.

Check for proper seismic restraints.

Check that safety valves have correct setting; greater than compressor discharge pressure, but not greater than pressure rating of system components.

Check that all operating controls are set for initial safe operation.

Starting Procedures:  Follow the manufacturer's written procedures and the following as a minimum:

Test generator at 50, 75, 100,and 125 percent load capacity using load banks at 100 percent power factor.

Run load test at all loads except 125 percent for 30 minutes recording engine and alternator readings at the start, at 15 minutes and at 30 minutes.  125 percent load to be run for 15 minutes recording readings at the start and end of test.

Simulate operation of all generator safeties such as high oil pressure, low oil pressure, high temperature, over speed, etc.  Observe function of safeties under actual malfunction situation.

Check for excessive vibration and noise.

acceptance criteria

Acceptance criteria for tests are indicated in the Specification Sections applicable to the systems being tested.  Unless indicated otherwise, acceptance criteria will be specified with the individual system, equipment, component, or device.

Training

Training requirements are specified in Division 01 Specifications and in Section 26 08 00 - Electrical Systems Commissioning.

END OF SECTION 26 08 13

Request for Start-up/fUNCTIONAL PERFORMANCE TEST

(Check applicable request below)

Request for Initial Startup ______		Request for Owner’s Demonstration ______

Project: _____________________________________	Project #:_____________________

Identification of Equipment or System:	_________________________________________

Location of Equipment or System:	_______________________________________________

Specification Section: ____________________	Detail/Drawing Number: _______________

Manufacturer / Supplier: ________________________________________________________

This Date: __________________	Inspection Requested for (Date): __________________

════════════════════════════════════════════════════════════

CONTRACTOR'S CERTIFICATION OF PERFORMANCE:

I hereby certify that the above described equipment or system, has been energized, operated, adjusted, and balanced in accordance with the requirements of the Contract Documents and the manufacturer's recommendations for a sufficient period to confirm that operation complies in all respects with the Contract Requirements.

__________________________________	____________________________	___________

Signature					Printed Name				Date

Installing Subcontractor:

__________________________________	____________________________	___________

Signature					Printed Name				Date

Manufacturer's Representative:  I hereby certify that I have been personally and actively involved with energizing, operational checkout, adjustments, and balancing of the above described equipment or system; and that such has been accomplished in accordance with the manufacturer's recommendations and is operating correctly.

__________________________________	____________________________	___________

# Signature  - Manufacturer's Representative	Printed Name	Date

════════════════════════════════════════════════════════════

CONFIRMATION or COMMENTS from BJC HEALTHCARE:

____________________________________________________________________________

Results of Test Acceptable? ____YES  ____NO	        Re-Test Required? ____YES  ____NO

Punch List:	____Attached		____To Follow		____N/A

System Acceptable for "User Training"? ____Yes	____No

__________________________________	____________________________	___________

Signature(s) – BJC HEALTHCARE –Facility Manager	Printed Name(s) – BJC HEALTHCARE		Date

__________________________________	____________________________	___________

Signature(s) – BJC HEALTHCARE – Project Manager	Printed Name(s) – BJC HEALTHCARE		Date

EXAMPLE - PREFUNCTIONAL CHECKLIST

Switchgear, Panelboards, Motor Control Centers, Transformers

Project: _____________________________________	Project #:_____________________

Identification of Equipment or System:	_________________________________________

Location of Equipment or System:	_______________________________________________

Specification Section: ____________________	Detail/Drawing Number: _______________

Manufacturer / Supplier: ________________________________________________________

This Date: __________________	Inspection Requested for (Date): __________________

════════════════════════════════════════════════════════════

Prefunctional Checklist Number: __________________

Components Included: ____Disconnects	____Fuses	____Meters	____Other

__________________________________________________

Associated Prefunctional Checklists:	__________________	__________________

- General:

  - The above systems and components integral to this equipment are complete and ready for Functional Performance Tests.  The Prefunctional Checklist items are complete and have been checked off only by parties having direct knowledge of the event, as indicted below, respective to each responsible contractor.  This Prefunctional Checklist is submitted for approval and is subject to the attached list of outstanding items not completed successfully.  Submit a Deficiency Form upon completion of any outstanding or deficient items.  None of the outstanding items preclude safe and reliable functional tests being performed.

  - ___ Deficiency Form attached.

  - This Prefunctional Checklist does not take the place of the manufacturer’s recommended checkout and Start-up procedures or report.

  - Contractors assigned responsibility for sections of the Prefunctional Checklist shall be responsible to ensure that their subcontractors complete and check off their Checklist items.

  - Prefunctional Checklist items shall be completed as part of Start-up and initial checkout, preparatory to functional testing.

| Contractor/Entity | Company | Abbreviation |
| --- | --- | --- |
| BJC HealthCare Staff |  | BJC HEALTHCARE |
| Architect/Engineer |  | AE |
| General Contractor / Construction Manager |  | GC |
| Mechanical Contractor |  | MC |
| Electrical Contractor |  | EC |
| Building Automation System Provider |  | BAS |
| Test, Adjust, and Balance Firm |  | TAB |
| Commissioning Consultant |  | CA |

- Requested Documentation Submitted:

| Specified Requirement | Yes | No | Date to be Submitted |
| --- | --- | --- | --- |
| a) | Manufacturer’s Product Data including Performance Data and Shop Drawings, as approved by Architect/Engineer |  |  |  |
| b) | Required Test Reports and/or Certifications |  |  |  |
| c) | Installation and Start-up Manual and Plan |  |  |  |
| d) | Wiring Diagrams, Control Schematics and Sequences |  |  |  |
| e) | Operating and Maintenance Manual Content for Applicable System |  |  |  |
| f) | Equipment List/Matrix |  |  |  |

- Equipment Verification:

| Item | Specified | Submitted | Installed |
| --- | --- | --- | --- |
| Manufacturer |  |  |  |
| Model Number |  |  |  |
| Serial Number |  |  |  |
| Service |  |  |  |
| Equipment Rating (amps) |  |  |  |
| Voltage/Phase |  |  |  |

- Installation Checks:

| a) Unit and General Installation | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Permanent labels affixed |  |  |  |
| 2. | Physical condition acceptable, no visible damage, cabinets in place |  |  |  |
| 3. | Properly mounted on equipment pad and anchored |  |  |  |
| 4. | Maintenance access acceptable |  |  |  |
| 5. | Interior clean and dry |  |  |  |
| 6. | Meter(s) installed per Contract Documents |  |  |  |
| 7. | Disconnects installed and labeled |  |  |  |
| 8. | Disconnects are pad lockable in open position |  |  |  |
| 9. | Circuit breakers installed and labeled |  |  |  |
| 10. | Fuses installed |  |  |  |
| 11. | Conduits installed and connected |  |  |  |
| 12. | Cable/conduit routing does not obstruct access |  |  |  |
| 13. | Equipment room properly ventilated, air-conditioned, heated, fire/smoke wall separated, fire/smoke dampered, fire sprinklered, fire alarmed and illuminated (normal, emergency and battery backed-up fixtures) |  |  |  |
| 14. | As-built drawings updated |  |  |  |

| b) Switchgear (service entrance 1500kVA and above) and Switchboards (service entrance less than 1500 kVA) | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Free standing metal enclosure |  |  |  |
| 2. | Cobber buses |  |  |  |
| 3. | Penetration to utility service area and equipment per code |  |  |  |

| c) Distribution Panelboards and other Panelboards | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Tin plated copper buses |  |  |  |
| 2. | Each circuit identified and labeled |  |  |  |
| 3. | Space for additional circuits exist |  |  |  |

| d) Motor Control Centers | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Tin plated copper buses |  |  |  |
| 2. | Main breakers installed and labeled |  |  |  |
| 3. | Each circuit identified and labeled |  |  |  |

| e) Transformers | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Dry type installed |  |  |  |
| 2. | Unit properly labeled and identified |  |  |  |

| f) Electrical and Controls | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Panel devices labeled and wiring tagged per Contract Documents |  |  |  |
| 2. | I/O devices labeled and wiring tagged per Contract Documents |  |  |  |
| 3. | Digital inputs and outputs operational |  |  |  |
| 4. | All electrical connections tight |  |  |  |
| 5. | Proper grounding installed for the electrical system, equipment, components, and unit |  |  |  |
| 6. | Safeties in place and operable |  |  |  |
| 7. | Sensors, transmitters, gages, etc., installed |  |  |  |
| 8. | Sensors calibrated (see below) |  |  |  |
| 9. | Control system interlocks hooked up and functional |  |  |  |
| 10. | All control devices and wiring complete |  |  |  |
| 11. | Lightning protection installed |  |  |  |
| 12. | Surge protection installed |  |  |  |

| g) Final | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Start-up report completed and attached with this Prefunctional Checklist |  |  |  |
| 2. | Safeties and safe operating ranges for this equipment have been reviewed and accepted |  |  |  |
| 3. | System is ready for Functional Performance Test |  |  |  |

- Operational Checks:

  - These checks supplement the manufacturer’s list.  This is not the Functional Performance Test.

| Operational Checks | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Associated Prefunctional Checklists are complete and accepted |  |  |  |
| 2. | Fuses are good |  |  |  |
| 3. | Resistance check(s) complete with results attached |  |  |  |
| 4. | Disconnect switch operates smoothly with full contact |  |  |  |
| 5. | Specified point-to-point checks have been completed and documentation record submitted for this system |  |  |  |

- Sensor and/or Actuator Calibration:

  - All field-installed temperature sensors, pressure sensors, meters, and gages, and all actuators and valves on this piece of equipment shall be calibrated.  Sensors installed in the unit at the factory with calibration certification provided are not required to be field calibrated.

  - All test instruments have had a certified calibration within the last 12-months:  Y / N

  - Sensor/Actuator Verification Table

| Sensor or Actuator | Correct Location (Y/N) (1) | Thermometer or Gage Value | BAS Value (2) | Instrument Measured Value (3) | Pass (Y/N) |
| --- | --- | --- | --- | --- | --- |

1)	Thermometer/Gage reading is the reading of the permanently mounted instrument on the equipment.

2)	BAS is the Building Automation System.  Instrument = testing instrument.

##### 3)	All sensors are calibrated within required tolerances	___ YES	___ NO

##### FINAL SIGN-OFF

Contractors attest that the above items have been verified and meet the requirements of the Contract Documents except as noted on the attached Deficiency form.

| General Contractor: | Print Name: |  |
| --- | --- | --- |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |
| Electrical Subcontractor | Print Name: |  |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |
| Other Subcontractor: | Print Name: |  |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |

Prefunctional Checklist received and reviewed for completeness by BJC HEALTHCARE representatives.   Functional Performance Test can proceed.

| BJC HEALTHCARE: | Print Name: |  |
| --- | --- | --- |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |
| BJC HEALTHCARE: | Print Name: |  |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |

EXAMPLE - PREFUNCTIONAL CHECKLIST

Emergency Power System

Project: _____________________________________	Project #:_____________________

Identification of Equipment or System:	_________________________________________

Location of Equipment or System:	_______________________________________________

Specification Section: ____________________	Detail/Drawing Number: _______________

Manufacturer / Supplier: ________________________________________________________

This Date: __________________	Inspection Requested for (Date): __________________

════════════════════════════════════════════════════════════

### Prefunctional Checklist Number: ___________

Components Included:

___ Prime Mover, ___ Generator, ___ Fuel System, ___Cooling System,  ___Battery System,

___ Exhaust System, ___ ATS, ___ UPS

Associated Prefunctional Checklists:

___Piping, ___ Pump, ___ Exhaust Fan, ___Other________________

- General:

- The above systems and components integral to this equipment are complete and ready for Functional Performance Tests.  The Prefunctional Checklist items are complete and have been checked off only by parties having direct knowledge of the event, as indicted below, respective to each responsible contractor.  This Prefunctional Checklist is submitted for approval and is subject to the attached list of outstanding items not completed successfully.  Submit a Deficiency Form upon completion of any outstanding or deficient items.  None of the outstanding items preclude safe and reliable functional tests being performed.

- ___ Deficiency Form attached.

- This Prefunctional Checklist does not take the place of the manufacturer’s recommended checkout and Start-up procedures or report.

- Contractors assigned responsibility for sections of the Prefunctional Checklist shall be responsible to ensure that their subcontractors complete and check off their Checklist items.

- Prefunctional Checklist items shall be completed as part of start-up and initial checkout, preparatory to functional testing.

| Contractor/Entity | Company | Abbreviation |
| --- | --- | --- |
| BJC HealthCare Staff |  | BJC HEALTHCARE |
| Architect/Engineer |  | AE |
| General Contractor / Construction Manager |  | GC |
| Mechanical Contractor |  | MC |
| Electrical Contractor |  | EC |
| Building Automation System Provider |  | BAS |
| Test, Adjust, and Balance Firm |  | TAB |
| Commissioning Consultant |  | CA |

- Requested Documentation Submitted:

| Specified Requirement | Yes | No | Date to be Submitted |
| --- | --- | --- | --- |
| a) | Manufacturer’s Product Data including Performance Data and Shop Drawings, as approved by Architect/Engineer |  |  |  |
| b) | Required Test Reports and/or Certifications |  |  |  |
| c) | Installation and Start-up Manual and Plan |  |  |  |
| d) | Wiring Diagrams, Control Schematics and Sequences |  |  |  |
| e) | Operating and Maintenance Manual Content for Applicable System |  |  |  |
| f) | Equipment List/Matrix |  |  |  |

- Equipment Verification:

| Item | Specified | Submitted | Installed |
| --- | --- | --- | --- |
| Manufacturer |  |  |  |
| Model Number |  |  |  |
| Serial Number |  |  |  |
| Service |  |  |  |
| Size/Rating (kW / continuous or standby) |  |  |  |
| Fuel Type |  |  |  |
| Voltage/Phase |  |  |  |

- Installation Checks:

| a) Unit and General Installation | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Permanent labels affixed |  |  |  |
| 2. | Physical condition acceptable |  |  |  |
| 3. | Properly mounted with vibration isolators |  |  |  |
| 4. | Factory alignment appears correct |  |  |  |
| 5. | Field alignment complete |  |  |  |
| 6. | Maintenance access acceptable |  |  |  |
| 7. | Fuel piping and/or prime mover exhaust system are properly supported (independent of prime mover and/or generator) |  |  |  |
| 8. | As-built drawings updated |  |  |  |
| 9. | Equipment clean |  |  |  |
| 10. | Equipment room properly ventilated, air-conditioned, heated, fire/smoke wall separated, fire/smoke dampered, fire sprinklered, fire alarmed and illuminated (normal, emergency and battery backed-up fixtures) |  |  |  |
| 11. | All equipment properly identified and labeled |  |  |  |

| b) Prime Mover | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Unit able to run on diesel fuel or a combination of natural gas and diesel fuel |  |  |  |
| 2. | Air cleaner and oil filter(s) installed |  |  |  |
| 3. | Vibration isolators active |  |  |  |
| 4. | Proper oil type used, with level correct |  |  |  |
| 5. | Exhaust duct installed with proper insulation and silencer/muffler |  |  |  |
| 6. | Exhaust system discharges to outside |  |  |  |
| 7. | Condensables able to be removed from exhaust system and discharged properly |  |  |  |
| 8. | Combustion and/or ventilation air louvers installed correctly |  |  |  |
| 9. | Cooling water radiator ducted to inlet louver |  |  |  |

| c) Generator | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Bearings lubricated |  |  |  |
| 2. | Rotor and stator in proper condition |  |  |  |
| 3. | Voltage regulator installed |  |  |  |
| 4. | Main breaker installed, rated at full load capacity |  |  |  |
| 5. | Instrument panel is mounted on unit |  |  |  |
| 6. | Remote annunciator panel installed |  |  |  |
| 7. | Generator auxiliary panel (dedicated to generator room equipment/lighting) is installed |  |  |  |

| d) Fuel System | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Piping Prefunctional Checklist complete and accepted |  |  |  |
| 2. | Day tank installed, with electric pump, hand pump, and bypass piping/valves |  |  |  |
| 3. | Above ground fuel tank installed, with pump(s) |  |  |  |
| 4. | Monitoring system installed |  |  |  |
| 5. | BJC HEALTHCARE Environmental reviews complete and accepted |  |  |  |

| e) Battery Charger and Batteries | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Batteries installed in a nonmetallic rack (wall mounted) adjacent to the prime mover |  |  |  |
| 2. | Battery electrolyte level is correct |  |  |  |
| 3. | Automatic trickle battery charger is installed (wall mounted) adjacent to battery bank |  |  |  |
| 4. | Battery cable connections are tight, terminals are clean |  |  |  |

| f) Automatic Transfer Switch | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | ATS rated for operation at the same output as the emergency generator, capacity is greater than total system transferred load |  |  |  |
| 2. | Transferred loads identified at panel, agrees with listed loads |  |  |  |
| 3. | ATS installation is complete |  |  |  |

| g) Electrical and Controls | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Panel devices labeled and wiring tagged per Contract Documents |  |  |  |
| 2. | Unit mounted instrument panel includes: |  |  |  |
|  | AC voltmeter |  |  |  |
|  | Ammeter |  |  |  |
|  | V-a selector switch |  |  |  |
|  | Frequency meter |  |  |  |
|  | Running time meter |  |  |  |
|  | Voltage adjusting rheostat |  |  |  |
|  | Exciter overload protection |  |  |  |
|  | Warning lights and alarms |  |  |  |
| 3. | Batteries provided with electronic sensing device for remote notification of battery conditions |  |  |  |
| 4. | I/O devices labeled and wiring tagged per Contract Documents |  |  |  |
| 5. | Digital inputs and outputs operational |  |  |  |
| 6. | All electrical connections tight |  |  |  |
| 7. | Proper grounding installed for the electrical system, equipment, components, and unit |  |  |  |
| 8. | Safeties in place and operable |  |  |  |
| 9. | Sensors, transmitters, gages, etc., installed |  |  |  |
| 10. | Sensors calibrated (see below) |  |  |  |
| 11. | Control system interlocks hooked up and functional |  |  |  |
| 12. | All control devices and wiring complete |  |  |  |
| 13. | Lightning protection installed |  |  |  |

| h) Final | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Start-up report completed and attached with this Prefunctional Checklist |  |  |  |
| 2. | List of items/systems served by the emergency power system is attached |  |  |  |
| 3. | Fuel tank(s) full |  |  |  |
| 4. | Safeties and safe operating ranges for this equipment have been reviewed and accepted |  |  |  |
| 5. | Sequence of operation adequately indicates all information |  |  |  |
| 6. | System is ready for Functional Performance Test |  |  |  |

- Operational Checks:

- These checks supplement the manufacturer’s list.  This is not the Functional Performance Test.

| Operational Checks | Yes | No | Comments |
| --- | --- | --- | --- |
| 1. | Associated Prefunctional Checklists are complete and accepted |  |  |  |
| 2. | ATS operates correctly |  |  |  |
| 3. | Resistance check(s) complete with results attached |  |  |  |
| 4. | Fuel system operates correctly |  |  |  |
| 5. | Ignition and battery systems operate correctly |  |  |  |
| 6. | Cooling system operates correctly |  |  |  |
| 7. | Specified point-to-point checks have been completed and documentation record submitted for this system |  |  |  |

- Sensor and/or Actuator Calibration:

- All field-installed temperature sensors, pressure sensors, meters, and gages, and all actuators and valves on this piece of equipment shall be calibrated.  Sensors installed in the unit at the factory with calibration certification provided are not required to be field calibrated.

- All test instruments have had a certified calibration within the last 12-months:  Y / N

| Sensor/Actuator Verification Table |
| --- |
| Sensor or Actuator | Correct Location (Y/N) (1) | Thermometer or Gage Value | BAS Value (2) | Instrument Measured Value (3) | Pass (Y/N) |

1. Thermometer/Gage reading is the reading of the permanently mounted instrument on the equipment.

2.  BAS is the Building Automation System.  Instrument = testing instrument.

##### 3.  All sensors are calibrated within required tolerances  ___ YES   ___ NO

##### FINAL SIGN-OFF

Contractors attest that the above items have been verified and meet the requirements of the Contract Documents except as noted on the attached Deficiency form.

| General Contractor: | Print Name: |  |
| --- | --- | --- |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |
| Electrical Subcontractor | Print Name: |  |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |
| Other Subcontractor: | Print Name: |  |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |

Prefunctional Checklist received and reviewed for completeness by BJC HEALTHCARE representatives.   Functional Performance Test can proceed.

| BJC HEALTHCARE: | Print Name: |  |
| --- | --- | --- |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |
| BJC HEALTHCARE: | Print Name: |  |
|  | Signature: |  |
|  | Title: |  |
|  | Date: |  |