SECTION 26 27 26 – wiring devices

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

This Section specifies the requirements for wiring devices (wall switches, receptacles, device plate covers, wall dimmers).

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

NEMA WD 1 - General-Purpose Wiring Devices.

NEMA WD 2 - Semiconductor Dimmers for Incandescent Lamps.

NEMA WD 5 - Specific-Purpose wiring Devices.

Americans with Disabilities Act (ADA).

ANSI/UL 20 - General Use Snap Switches.

ANSI/UL 498 - Attachment Plugs and Receptacles.

ANSI/UL 943- Ground Fault Circuit Interrupters.

SUBMITTALS

Product Data:

Submit manufacturer's product data for all wiring devices and floor boxes.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Provide factory fabricated wiring devices in the type and electrical rating for the service indicated. Where type and grade are not indicated provide proper selection to correspond with branch circuit wiring and overcurrent protection.

Attachment of wires to devices shall be by screw pressure under the head of binding screws. Arrangements depending on spring pressure or tension are not acceptable. All binding screws shall be brass or bronze.

Manufacturers

Wall Dimmers:

Lutron.

Leviton.

Lighting Occupancy Sensors:

Wattstopper.

Novitas.

Other manufacturers as specifically approved in writing by Owner.

wall switches

Type:  Quiet type, back and side wired switches as specified herein.

Rating:  20 amperes, 120/277 volts.

Listing:  UL 20 and Federal Specification W-S-896.

Manufacturers:  Provide devices in the color as specified herein.

| Type | Pass & Seymour | Arrow Hart | Leviton | Thomas & Betts | Hubbell |
| --- | --- | --- | --- | --- | --- |
| S | 20AC1 | 1991 | 1221-2 |  |  |
| S2 | 20AC2 | 1992 | 1222-2 |  |  |
| S3 | 20AC3 | 1993 | 1223-2 |  |  |
| S4 | 20AC4 | 1994 | 1224-2 |  |  |

*Provide color designation for designated use.

Receptacles

Type:  Hospital Grade, where identified on Drawings.  Back and side wired receptacles, as specified herein.

Rating:  Scheduled on Drawings.

Listing:  UL 498 and Federal Specification W-C-596.

Provide devices in the color as specified herein.

| NEMA Configuration | Pass & Seymour | Arrow Hart | Leviton |
| --- | --- | --- | --- |
| 5-20R (Duplex) | 9300-HG | 8300 | 8300 |
| 5-20R (Single) | 9301-HG | 8301 | 8310 |
| 5-20R (Tamper Resistant) | SG-3-H | TR-83 | ------ |
| GFCI | 2091-SHG | GF-8300 | 6898-HG |

*Provide color designation for designated use.

E.  All receptacles within six (6) feet of a water source such as sinks shall be a GFCl receptacle. Feed through to non-GFCI receptacles is not permitted.

Device plates

Laboratories and Patient Care Areas:  Use 302 stainless steel.

Finished Office Areas:  Nylon in color as selected by Architect.

Exposed Boxes in Dry Interior Spaces:

Manufacture plates of heavy cadmium-plated sheet steel.

Edges of plates must be flush with edges of boxes.

Other Areas:

Use weatherproof device plates.

Provide cast plates with gasketed spring door covers for protection of device.

For outlets and switches, provide labeled nameplates listing power source and circuit number. Example:  P10 for panel “P” circuit “10”. Label to be tape type black letters on white for normal power and red on white for all generator/emergency circuits.

Covers for outlets outdoors shall meet the requirements of latest NEC.

Device color

All switches shall be white except as follows:  Red switches shall be used on all equipment and circuits connected to emergency power.

Normal power receptacles shall be white and receptacles connected to the emergency electrical circuits shall be red.

In laboratories, normal power receptacles shall have alternating colors for different circuits (gray, brown and white).

Isolated ground receptacles shall be orange.

Wall dimmers

Wall dimmers shall be linear slide type equal to Lutron Nova Series.

Dimmers shall be 600 watts minimum, incandescent, larger size as required to accommodate greater connected loads.

Light occupancy sensors

Lighting occupancy sensors shall be installed as a functioning system per the Contract Documents and manufacturer’s installation instructions.

Proper commissioning shall be completed prior to Substantial Completion.

Ultrasonic motion detectors shall not be used in vivarium corridors.

Telecommunication outlets

Telecommunication outlets, boxes, sleeves and conduit are part of this Contract.

Provide outlet boxes and 1-inch conduit with connector and bushing to accessible location above the ceiling.

Provide a pull string in each conduit and tie off pull string above ceiling.

For floor outlets, provide 1-inch conduit to accessible location above the ceiling on the floor served by the outlet.

EXECUTION

PREPARATION

Contractor must examine the areas and conditions under which wiring devices are to be installed and notify the Owner’s Project Manager in writing of conditions detrimental to the proper and timely completion of the Work.

Inspect devices for physical damage.

Do not proceed with the Work until unsatisfactory conditions have been corrected.

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Wall switch and receptacle ground wiring shall terminate at the wiring device with an insulated tin-plated copper spade compression terminal.  Select a spade terminal compatible with the wiring devices supplied so that device screw terminals can be torqued to the wiring device manufacturer's recommendations

Wall receptacles shall be installed with the ground pinhole in the up position, unless instructed otherwise by the Owner.

The approximate location of switches and receptacles are indicated on the Drawings.  These Drawings, however, may not give complete and accurate information in regard to locations of such items.  Determine exact locations by reference to the architectural Drawings and by actual measurements during construction of the building before rough-in, subject to the approval of the Owner’s Project Manager.

Install wall switches 48 inches above finished floor, OFF position down.

Install wall dimmers 48 inches above floor; derate ganged dimmers as instructed by manufacturer; do not use common neutral.

Where wainscot is near the 48 inch level, install device in the wall below the top edge of the wainscot and as near the 48 inch level as possible to provide the most pleasing appearance.  Do not partially install devices in the wainscot and partially in the wall.

Where shown the strike side of doors, install switches and dimmers not less than 2 inches and not more than 12 inches from door trim, but in all cases as close to the 2 inch setback as possible.

Verify all doors swings before rough-in and locate switches and dimmers on strike side of door wherever possible.

Position the center of convenience, telephone, computer and TV outlets 18 inches above floor or 8 inches above countertops unless otherwise noted.  Coordinate with equipment and architectural Drawings.  Install outlets vertically on walls and horizontally above countertops.

Install specific-use receptacles at heights shown on Drawings.

END OF SECTION 26 27 26